## Details of Source Heater
Name | Node Type | Max output rate [kW] | Type | Cost for kW for 55 °C output | Cost for kW for 67 °C output | Cost for kW for 80 °C output
Sarfvik | Source/Heater | 40000 | Biomass boiler | 1000 | 1200 | 1500
Kirkkonummi | Source/Heater | 20000 | Natural gas boiler | 500 | 600 | 900
Ericsson | Source/Heater | 2000 | Heat pump for heating only return water | ?? | ?? | ??

## Details of Sink-User Nodes
Name | X-Coordinate | Y-Coordinate | Category | Priority | Base Demand [kW] | Base Demand [kg/s] | Demand 00-01 | Demand 01-02 | Demand 02-03 | Demand 03-04 | Demand 04-05 | Demand 05-06 | Demand 06-07 | Demand 07-08 | Demand 08-09 | Demand 09-10 | Demand 10-11 | Demand 11-12 | Demand 12-13 | Demand 13-14 | Demand 14-15 | Demand 15-16 | Demand 16-17 | Demand 17-18 | Demand 18-19 | Demand 19-20 | Demand 20-21 | Demand 21-22 | Demand 22-23 | Demand 23-00
Junction-128231 | 362739.6094 | 6671054.5859 | Rivitalot | 100 | 40.333 | 0.193 | 4.609 | 4.5566 | 4.5304 | 4.5042 | 4.5304 | 4.5828 | 4.7399 | 4.8447 | 4.8185 | 4.7138 | 4.6876 | 4.5042 | 4.4257 | 4.3733 | 4.3471 | 4.3733 | 4.4257 | 4.5042 | 4.5566 | 4.6352 | 4.7138 | 4.7661 | 4.7138 | 4.6352
Junction-128433 | 363145.9336 | 6672008.9297 | Omakotitalot | 100 | 7 | 0.033413 | 0.78563 | 0.78563 | 0.78563 | 0.78563 | 0.78563 | 0.78563 | 0.81181 | 0.838 | 0.838 | 0.81181 | 0.81181 | 0.78563 | 0.75944 | 0.75944 | 0.75944 | 0.75944 | 0.75944 | 0.78563 | 0.78563 | 0.81181 | 0.81181 | 0.838 | 0.81181 | 0.81181
Junction-122930 | 357952.6719 | 6668109.0352 | Muut urheilu- ja liikuntaraken | 100 | 716.667 | 3.4208 | 81.6788 | 81.0241 | 80.5528 | 80.2123 | 80.5528 | 81.6003 | 84.0357 | 86.2616 | 85.5284 | 83.7214 | 83.4072 | 79.8981 | 78.7458 | 77.6983 | 77.4364 | 77.6198 | 78.4316 | 79.8981 | 81.0241 | 82.4906 | 83.8786 | 84.4547 | 83.7214 | 82.5692
Neidonkallio_EMP_2 | 357457.5742 | 6669242.1914 | Rivitalot | 100 | 60 | 0.2864 | 6.8349 | 6.7826 | 6.7302 | 6.704 | 6.7302 | 6.8349 | 7.0444 | 7.2278 | 7.1492 | 7.0183 | 6.9921 | 6.6778 | 6.5993 | 6.4945 | 6.4945 | 6.4945 | 6.5731 | 6.6778 | 6.7826 | 6.9135 | 7.0183 | 7.0706 | 7.0183 | 6.9135
Neidonkallio_EMP_1 | 357047.3125 | 6669431.2383 | Omakotitalot | 100 | 12 | 0.057279 | 1.3618 | 1.3618 | 1.3356 | 1.3356 | 1.3356 | 1.3618 | 1.4141 | 1.4403 | 1.4403 | 1.4141 | 1.3879 | 1.3356 | 1.3094 | 1.3094 | 1.3094 | 1.3094 | 1.3094 | 1.3356 | 1.3618 | 1.3879 | 1.4141 | 1.4141 | 1.4141 | 1.3879
Kummihovi_EMP | 355672.4883 | 6664548.4023 | Asuinkerrostalot | 100 | 177 | 0.84487 | 20.1644 | 20.0073 | 19.9025 | 19.8239 | 19.9025 | 20.1644 | 20.7667 | 21.2904 | 21.1333 | 20.6881 | 20.6096 | 19.7192 | 19.4573 | 19.1954 | 19.1169 | 19.1693 | 19.3788 | 19.7192 | 20.0073 | 20.3739 | 20.7143 | 20.8714 | 20.6881 | 20.4001
Kantvik_EMP | 355459.8828 | 6664662.2539 | Rivitalot | 100 | 64 | 0.30549 | 7.3063 | 7.2278 | 7.2016 | 7.1754 | 7.2016 | 7.2801 | 7.5158 | 7.6991 | 7.6468 | 7.4896 | 7.4373 | 7.123 | 7.0444 | 6.9397 | 6.9135 | 6.9397 | 6.9921 | 7.123 | 7.2278 | 7.3587 | 7.4896 | 7.542 | 7.4896 | 7.3849
Junction-99936 | 356821.457 | 6668012.3281 | Omakotitalot | 100 | 5 | 0.023866 | 0.57612 | 0.57612 | 0.54994 | 0.54994 | 0.54994 | 0.57612 | 0.57612 | 0.60231 | 0.60231 | 0.57612 | 0.57612 | 0.54994 | 0.54994 | 0.54994 | 0.54994 | 0.54994 | 0.54994 | 0.54994 | 0.57612 | 0.57612 | 0.57612 | 0.60231 | 0.57612 | 0.57612
Junction-99902 | 357003.668 | 6668326.707 | Omakotitalot | 100 | 11 | 0.052506 | 1.257 | 1.2308 | 1.2308 | 1.2308 | 1.2308 | 1.257 | 1.2832 | 1.3356 | 1.3094 | 1.2832 | 1.2832 | 1.2308 | 1.2046 | 1.2046 | 1.1784 | 1.1784 | 1.2046 | 1.2308 | 1.2308 | 1.257 | 1.2832 | 1.3094 | 1.2832 | 1.257
Junction-99881 | 356756.1289 | 6667989.7422 | Omakotitalot | 100 | 4 | 0.019093 | 0.44519 | 0.44519 | 0.44519 | 0.44519 | 0.44519 | 0.44519 | 0.47138 | 0.47138 | 0.47138 | 0.47138 | 0.47138 | 0.44519 | 0.44519 | 0.44519 | 0.44519 | 0.44519 | 0.44519 | 0.44519 | 0.44519 | 0.47138 | 0.47138 | 0.47138 | 0.47138 | 0.47138
Junction-99878 | 356756.375 | 6668030.9883 | Omakotitalot | 100 | 9 | 0.042959 | 1.0213 | 1.0213 | 1.0213 | 0.99513 | 1.0213 | 1.0213 | 1.0475 | 1.0737 | 1.0737 | 1.0475 | 1.0475 | 0.99513 | 0.99513 | 0.96894 | 0.96894 | 0.96894 | 0.99513 | 0.99513 | 1.0213 | 1.0475 | 1.0475 | 1.0737 | 1.0475 | 1.0475
Junction-99877 | 356754.5625 | 6668051.168 | Omakotitalot | 100 | 6 | 0.02864 | 0.68088 | 0.68088 | 0.68088 | 0.68088 | 0.68088 | 0.68088 | 0.70706 | 0.73325 | 0.70706 | 0.70706 | 0.70706 | 0.68088 | 0.65469 | 0.65469 | 0.65469 | 0.65469 | 0.65469 | 0.68088 | 0.68088 | 0.68088 | 0.70706 | 0.70706 | 0.70706 | 0.68088
Junction-102637 | 356957.9648 | 6665836.2617 | Omakotitalot | 100 | 8 | 0.038186 | 0.91656 | 0.91656 | 0.89038 | 0.89038 | 0.89038 | 0.91656 | 0.94275 | 0.96894 | 0.94275 | 0.94275 | 0.94275 | 0.89038 | 0.89038 | 0.86419 | 0.86419 | 0.86419 | 0.86419 | 0.89038 | 0.91656 | 0.91656 | 0.94275 | 0.94275 | 0.94275 | 0.91656
Junction-100269 | 357087.4531 | 6668411.9609 | Omakotitalot | 100 | 4 | 0.019093 | 0.44519 | 0.44519 | 0.44519 | 0.44519 | 0.44519 | 0.44519 | 0.47138 | 0.47138 | 0.47138 | 0.47138 | 0.47138 | 0.44519 | 0.44519 | 0.44519 | 0.44519 | 0.44519 | 0.44519 | 0.44519 | 0.44519 | 0.47138 | 0.47138 | 0.47138 | 0.47138 | 0.47138
Junction-100267 | 357293.6016 | 6667631.6133 | Asuinkerrostalot | 100 | 83.333 | 0.39777 | 9.5061 | 9.4275 | 9.3751 | 9.3228 | 9.3751 | 9.4799 | 9.7679 | 10.0298 | 9.9513 | 9.7418 | 9.6894 | 9.2966 | 9.1656 | 9.0347 | 9.0085 | 9.0347 | 9.1133 | 9.2966 | 9.4275 | 9.5846 | 9.7418 | 9.8203 | 9.7418 | 9.6108
Junction-100264 | 357244.7031 | 6667637.9844 | Asuinkerrostalot | 100 | 66 | 0.31504 | 7.5158 | 7.4634 | 7.4111 | 7.3849 | 7.4111 | 7.5158 | 7.7515 | 7.9348 | 7.8824 | 7.6991 | 7.6729 | 7.3587 | 7.2539 | 7.1492 | 7.123 | 7.1492 | 7.2278 | 7.3587 | 7.4634 | 7.5944 | 7.7253 | 7.7777 | 7.6991 | 7.5944
Junction-100262 | 357124.9766 | 6668437.125 | Rivitalot | 100 | 53 | 0.25298 | 6.0493 | 5.9969 | 5.9446 | 5.9446 | 5.9446 | 6.0231 | 6.2064 | 6.3898 | 6.3112 | 6.1803 | 6.1803 | 5.9184 | 5.8136 | 5.7351 | 5.7351 | 5.7351 | 5.7874 | 5.9184 | 5.9969 | 6.1017 | 6.2064 | 6.2588 | 6.1803 | 6.1017
Junction-100261 | 357124.9102 | 6667954.5312 | Asuinkerrostalot | 100 | 83.333 | 0.39777 | 9.5061 | 9.4275 | 9.3751 | 9.3228 | 9.3751 | 9.4799 | 9.7679 | 10.0298 | 9.9513 | 9.7418 | 9.6894 | 9.2966 | 9.1656 | 9.0347 | 9.0085 | 9.0347 | 9.1133 | 9.2966 | 9.4275 | 9.5846 | 9.7418 | 9.8203 | 9.7418 | 9.6108
Junction-100249 | 356772.1602 | 6668078.7109 | Omakotitalot | 100 | 4 | 0.019093 | 0.44519 | 0.44519 | 0.44519 | 0.44519 | 0.44519 | 0.44519 | 0.47138 | 0.47138 | 0.47138 | 0.47138 | 0.47138 | 0.44519 | 0.44519 | 0.44519 | 0.44519 | 0.44519 | 0.44519 | 0.44519 | 0.44519 | 0.47138 | 0.47138 | 0.47138 | 0.47138 | 0.47138
Junction-100247 | 356771.3203 | 6668092.5078 | Omakotitalot | 100 | 5 | 0.023866 | 0.57612 | 0.57612 | 0.54994 | 0.54994 | 0.54994 | 0.57612 | 0.57612 | 0.60231 | 0.60231 | 0.57612 | 0.57612 | 0.54994 | 0.54994 | 0.54994 | 0.54994 | 0.54994 | 0.54994 | 0.54994 | 0.57612 | 0.57612 | 0.57612 | 0.60231 | 0.57612 | 0.57612
Junction-100241 | 357044.0625 | 6667743.3047 | Omakotitalot | 100 | 6 | 0.02864 | 0.68088 | 0.68088 | 0.68088 | 0.68088 | 0.68088 | 0.68088 | 0.70706 | 0.73325 | 0.70706 | 0.70706 | 0.70706 | 0.68088 | 0.65469 | 0.65469 | 0.65469 | 0.65469 | 0.65469 | 0.68088 | 0.68088 | 0.68088 | 0.70706 | 0.70706 | 0.70706 | 0.68088
Junction-100240 | 357051.4219 | 6667738.6992 | Omakotitalot | 100 | 6 | 0.02864 | 0.68088 | 0.68088 | 0.68088 | 0.68088 | 0.68088 | 0.68088 | 0.70706 | 0.73325 | 0.70706 | 0.70706 | 0.70706 | 0.68088 | 0.65469 | 0.65469 | 0.65469 | 0.65469 | 0.65469 | 0.68088 | 0.68088 | 0.68088 | 0.70706 | 0.70706 | 0.70706 | 0.68088
Junction-100231 | 357204 | 6667925.1367 | Asuinkerrostalot | 100 | 84.667 | 0.40414 | 9.6632 | 9.5846 | 9.5061 | 9.4799 | 9.5061 | 9.637 | 9.9251 | 10.1869 | 10.1084 | 9.8989 | 9.8465 | 9.4275 | 9.2966 | 9.1656 | 9.1394 | 9.1656 | 9.2704 | 9.4275 | 9.5846 | 9.7418 | 9.8989 | 9.9774 | 9.8989 | 9.7679
Junction-100229 | 357257.8242 | 6667948.8945 | Asuinkerrostalot | 100 | 75 | 0.358 | 8.5371 | 8.4848 | 8.4324 | 8.4062 | 8.4324 | 8.5371 | 8.799 | 9.0347 | 8.9561 | 8.7728 | 8.7204 | 8.3538 | 8.2491 | 8.1181 | 8.0919 | 8.1181 | 8.1967 | 8.3538 | 8.4848 | 8.6419 | 8.7728 | 8.8514 | 8.7728 | 8.6419
Junction-100227 | 357263.3008 | 6667937.6133 | Rivitalot | 100 | 49 | 0.23389 | 5.5779 | 5.5518 | 5.4994 | 5.4732 | 5.4994 | 5.5779 | 5.7351 | 5.8922 | 5.8398 | 5.7351 | 5.7089 | 5.4732 | 5.3946 | 5.3161 | 5.2899 | 5.3161 | 5.3684 | 5.4732 | 5.5518 | 5.6303 | 5.7351 | 5.7874 | 5.7351 | 5.6565
Junction-100220 | 357324.957 | 6667955.4531 | Asuinkerrostalot | 100 | 52.333 | 0.2498 | 5.9707 | 5.9184 | 5.8922 | 5.866 | 5.8922 | 5.9708 | 6.1279 | 6.3112 | 6.2326 | 6.1017 | 6.1017 | 5.8398 | 5.7613 | 5.6827 | 5.6565 | 5.6565 | 5.7351 | 5.8398 | 5.9184 | 6.0231 | 6.1279 | 6.1803 | 6.1017 | 6.0231
Junction-100179 | 357150.9961 | 6668037.7578 | Omakotitalot | 100 | 14 | 0.066826 | 1.5974 | 1.5713 | 1.5713 | 1.5713 | 1.5713 | 1.5974 | 1.6498 | 1.676 | 1.676 | 1.6236 | 1.6236 | 1.5713 | 1.5451 | 1.5189 | 1.5189 | 1.5189 | 1.5451 | 1.5713 | 1.5713 | 1.6236 | 1.6498 | 1.6498 | 1.6236 | 1.6236
Junction-100172 | 357738.6094 | 6668505.4336 | Rivitalot | 100 | 54.667 | 0.26094 | 6.2326 | 6.1803 | 6.1541 | 6.1279 | 6.1541 | 6.2326 | 6.4159 | 6.5731 | 6.5207 | 6.3898 | 6.3636 | 6.1017 | 5.9969 | 5.9184 | 5.9184 | 5.9184 | 5.9708 | 6.1017 | 6.1803 | 6.285 | 6.3898 | 6.4421 | 6.3898 | 6.3112
Junction-100168 | 357338.0391 | 6668528.5273 | Asuinkerrostalot | 100 | 63.667 | 0.3039 | 7.2539 | 7.2016 | 7.1492 | 7.123 | 7.1492 | 7.2539 | 7.4634 | 7.6729 | 7.5944 | 7.4373 | 7.4111 | 7.0968 | 6.9921 | 6.9135 | 6.8873 | 6.8873 | 6.9659 | 7.0968 | 7.2016 | 7.3325 | 7.4634 | 7.5158 | 7.4373 | 7.3325
Junction-100156 | 357969.4805 | 6667286.582 | Tukku- ja vähittäiskaupan myym | 100 | 666.667 | 3.1822 | 75.9961 | 75.3676 | 74.9224 | 74.6082 | 74.9224 | 75.9176 | 78.1959 | 80.2385 | 79.5576 | 77.8816 | 77.5674 | 74.3201 | 73.2464 | 72.2775 | 72.0418 | 72.1989 | 72.9584 | 74.3201 | 75.3676 | 76.7556 | 78.0388 | 78.5625 | 77.8816 | 76.8079
Junction-100124 | 357135.7109 | 6667187.8633 | Yleiskäyttöiset teollisuushall | 100 | 172.667 | 0.82419 | 19.693 | 19.5359 | 19.4049 | 19.3264 | 19.4049 | 19.6668 | 20.2429 | 20.7929 | 20.6096 | 20.1644 | 20.0858 | 19.2478 | 18.9859 | 18.7241 | 18.6717 | 18.6979 | 18.9074 | 19.2478 | 19.5359 | 19.8763 | 20.2168 | 20.3477 | 20.1644 | 19.9025
Junction-100111 | 357182.0195 | 6667709.7109 | Rivitalot | 100 | 57.333 | 0.27367 | 6.5469 | 6.4945 | 6.4421 | 6.4159 | 6.4421 | 6.5207 | 6.7302 | 6.8873 | 6.8349 | 6.704 | 6.6778 | 6.3898 | 6.3112 | 6.2064 | 6.2064 | 6.2064 | 6.285 | 6.3898 | 6.4945 | 6.5993 | 6.704 | 6.7564 | 6.704 | 6.5993
Junction-100107 | 357177.8594 | 6667665.1641 | Rivitalot | 100 | 103 | 0.49165 | 11.732 | 11.6534 | 11.5749 | 11.5225 | 11.5749 | 11.732 | 12.0724 | 12.3867 | 12.2819 | 12.0201 | 11.9939 | 11.4701 | 11.313 | 11.1559 | 11.1297 | 11.1559 | 11.2606 | 11.4701 | 11.6534 | 11.8629 | 12.0463 | 12.151 | 12.0201 | 11.8629
Junction-100105 | 356997.7969 | 6667811.8594 | Omakotitalot | 100 | 9 | 0.042959 | 1.0213 | 1.0213 | 1.0213 | 0.99513 | 1.0213 | 1.0213 | 1.0475 | 1.0737 | 1.0737 | 1.0475 | 1.0475 | 0.99513 | 0.99513 | 0.96894 | 0.96894 | 0.96894 | 0.99513 | 0.99513 | 1.0213 | 1.0475 | 1.0475 | 1.0737 | 1.0475 | 1.0475
Junction-100104 | 357013.6641 | 6667796.9023 | Omakotitalot | 100 | 4 | 0.019093 | 0.44519 | 0.44519 | 0.44519 | 0.44519 | 0.44519 | 0.44519 | 0.47138 | 0.47138 | 0.47138 | 0.47138 | 0.47138 | 0.44519 | 0.44519 | 0.44519 | 0.44519 | 0.44519 | 0.44519 | 0.44519 | 0.44519 | 0.47138 | 0.47138 | 0.47138 | 0.47138 | 0.47138
Junction-100103 | 357036.0547 | 6667834.0859 | Omakotitalot | 100 | 8 | 0.038186 | 0.91656 | 0.91656 | 0.89038 | 0.89038 | 0.89038 | 0.91656 | 0.94275 | 0.96894 | 0.94275 | 0.94275 | 0.94275 | 0.89038 | 0.89038 | 0.86419 | 0.86419 | 0.86419 | 0.86419 | 0.89038 | 0.91656 | 0.91656 | 0.94275 | 0.94275 | 0.94275 | 0.91656
Junction-100102 | 357036.4766 | 6667819.4492 | Omakotitalot | 100 | 9 | 0.042959 | 1.0213 | 1.0213 | 1.0213 | 0.99513 | 1.0213 | 1.0213 | 1.0475 | 1.0737 | 1.0737 | 1.0475 | 1.0475 | 0.99513 | 0.99513 | 0.96894 | 0.96894 | 0.96894 | 0.99513 | 0.99513 | 1.0213 | 1.0475 | 1.0475 | 1.0737 | 1.0475 | 1.0475
Junction-100100 | 357719.6914 | 6667387.2617 | Toimistorakennukset | 100 | 173.333 | 0.82737 | 19.7454 | 19.5883 | 19.4835 | 19.4049 | 19.4835 | 19.7454 | 20.3215 | 20.8714 | 20.6881 | 20.2429 | 20.1644 | 19.3264 | 19.0383 | 18.8026 | 18.7241 | 18.7764 | 18.9598 | 19.3264 | 19.5883 | 19.9549 | 20.2953 | 20.4263 | 20.2429 | 19.9811
Junction-100098 | 357691.707 | 6667372.5508 | Tukku- ja vähittäiskaupan myym | 100 | 37.667 | 0.17979 | 4.2948 | 4.2686 | 4.2424 | 4.2162 | 4.2424 | 4.2948 | 4.4257 | 4.5304 | 4.5042 | 4.3995 | 4.3733 | 4.19 | 4.1376 | 4.0853 | 4.0591 | 4.0853 | 4.1114 | 4.19 | 4.2686 | 4.3471 | 4.3995 | 4.4519 | 4.3995 | 4.3471
Junction-100096 | 357682.9375 | 6667369.2148 | Toimistorakennukset | 100 | 43.667 | 0.20843 | 4.9756 | 4.9494 | 4.8971 | 4.8971 | 4.8971 | 4.9756 | 5.1328 | 5.2637 | 5.2113 | 5.1066 | 5.0804 | 4.8709 | 4.7923 | 4.7399 | 4.7138 | 4.7399 | 4.7661 | 4.8709 | 4.9494 | 5.028 | 5.1066 | 5.1589 | 5.1066 | 5.028
Junction-100058 | 357453.1523 | 6668007.7148 | Asuinkerrostalot | 100 | 222 | 1.0597 | 25.2971 | 25.1138 | 24.9567 | 24.8519 | 24.9567 | 25.2709 | 26.0304 | 26.7113 | 26.5018 | 25.9256 | 25.8209 | 24.7472 | 24.4068 | 24.0663 | 23.9878 | 24.0401 | 24.302 | 24.7472 | 25.1138 | 25.559 | 25.978 | 26.1613 | 25.9256 | 25.5852
Junction-100054 | 357388.9688 | 6668000.9531 | Asuinkerrostalot | 100 | 85 | 0.40573 | 9.6894 | 9.6108 | 9.5584 | 9.5061 | 9.5584 | 9.6894 | 9.9774 | 10.2393 | 10.1346 | 9.9251 | 9.8989 | 9.4799 | 9.3489 | 9.218 | 9.1918 | 9.1918 | 9.2966 | 9.4799 | 9.6108 | 9.7941 | 9.9513 | 10.0298 | 9.9251 | 9.7941
Junction-100052 | 357344.3984 | 6668002.582 | Asuinkerrostalot | 100 | 43.333 | 0.20684 | 4.9494 | 4.8971 | 4.8709 | 4.8447 | 4.8709 | 4.9233 | 5.0804 | 5.2113 | 5.1589 | 5.0542 | 5.0542 | 4.8185 | 4.7661 | 4.6876 | 4.6876 | 4.6876 | 4.7399 | 4.8185 | 4.8971 | 4.9756 | 5.0804 | 5.1066 | 5.0542 | 5.0018
Junction-100043 | 357762.6016 | 6667876.0078 | Muut myymälärakennukset | 100 | 79.947 | 0.38161 | 9.1133 | 9.0347 | 8.9823 | 8.9561 | 8.9823 | 9.1133 | 9.3751 | 9.6108 | 9.5323 | 9.3489 | 9.2966 | 8.9038 | 8.7728 | 8.6681 | 8.6419 | 8.6681 | 8.7466 | 8.9038 | 9.0347 | 9.1918 | 9.3489 | 9.4275 | 9.3489 | 9.218
Junction-100042 | 357675.8984 | 6667918.8203 | Tukku- ja vähittäiskaupan myym | 100 | 159.667 | 0.76213 | 18.2003 | 18.0432 | 17.9384 | 17.8599 | 17.9384 | 18.1741 | 18.7241 | 19.2216 | 19.0645 | 18.6455 | 18.5669 | 17.8075 | 17.5456 | 17.3099 | 17.2576 | 17.2838 | 17.4671 | 17.8075 | 18.0432 | 18.3836 | 18.6979 | 18.8288 | 18.6455 | 18.4098
Junction-100039 | 356790.5664 | 6668110.2539 | Omakotitalot | 100 | 7 | 0.033413 | 0.78563 | 0.78563 | 0.78563 | 0.78563 | 0.78563 | 0.78563 | 0.81181 | 0.838 | 0.838 | 0.81181 | 0.81181 | 0.78563 | 0.75944 | 0.75944 | 0.75944 | 0.75944 | 0.75944 | 0.78563 | 0.78563 | 0.81181 | 0.81181 | 0.838 | 0.81181 | 0.81181
Junction-100019 | 357118.3086 | 6668419.9609 | Omakotitalot | 100 | 10 | 0.047733 | 1.1522 | 1.1261 | 1.1261 | 1.1261 | 1.1261 | 1.1261 | 1.1784 | 1.2046 | 1.2046 | 1.1784 | 1.1522 | 1.1261 | 1.0999 | 1.0737 | 1.0737 | 1.0737 | 1.0999 | 1.1261 | 1.1261 | 1.1522 | 1.1784 | 1.1784 | 1.1784 | 1.1522
Hommaksenkaari_EMP | 362957.4922 | 6672797.7812 | Rivitalot | 100 | 86.667 | 0.41368 | 9.8727 | 9.7941 | 9.7418 | 9.6894 | 9.7418 | 9.8727 | 10.1608 | 10.4226 | 10.3441 | 10.1346 | 10.0822 | 9.6632 | 9.5323 | 9.4013 | 9.3751 | 9.3751 | 9.4799 | 9.6632 | 9.7941 | 9.9774 | 10.1346 | 10.2131 | 10.1346 | 9.9774

## Node Connectivity Details
Name | Start Node | End Node | Length [m] | Heat Transfer Coefficient [W/mK] | Diameter [mm] | Has Supply Line | Has Return Line | Capacity [kW] | Capacity [kg/s]
Pipe-191 | Junction-165 | Junction-192 | 26.89 | 0.166 | 43.1 | true | true | 172 | 0.821
Pipe-696 | Junction-1395 | Junction-736 | 48.36 | 0.18 | 54.5 | true | true | 321 | 1.5322
Pipe-843 | Junction-897 | Junction-894 | 7.01 | 0.18 | 54.5 | true | true | 321 | 1.5322
Pipe-862 | Junction-916 | Junction-909 | 10.01 | 0.254 | 132.5 | true | true | 3354 | 16.0095
Pipe-865 | Junction-919 | Junction-920 | 0.39 | 0.483 | 210.1 | true | true | 11253 | 53.7136
Pipe-867 | Junction-916 | Junction-919 | 94.91 | 0.293 | 210.1 | true | true | 11253 | 53.7136
Pipe-876 | Junction-942 | Junction-1164 | 43.57 | 0.18 | 54.5 | true | true | 321 | 1.5322
Pipe-892 | Junction-954 | Junction-945 | 43.36 | 0.166 | 43.1 | true | true | 172 | 0.821
Pipe-925 | Junction-998 | Junction-956 | 64.94 | 0.166 | 43.1 | true | true | 172 | 0.821
Pipe-938 | Junction-998 | Junction-954 | 4 | 0.18 | 54.5 | true | true | 321 | 1.5322
Pipe-973 | Junction-1036 | Junction-916 | 33.26 | 0.293 | 210.1 | true | true | 11253 | 53.7136
Pipe-975 | Junction-1036 | Junction-907 | 1.08 | 0.293 | 210.1 | true | true | 11253 | 53.7136
Pipe-1055 | Junction-1143 | Junction-1124 | 28.46 | 0.166 | 43.1 | true | true | 172 | 0.821
Pipe-1088 | Junction-1044 | Junction-1114 | 51.3 | 0.18 | 54.5 | true | true | 321 | 1.5322
Pipe-1324 | Junction-1395 | Junction-1396 | 36.98 | 0.282 | 160.3 | true | true | 5533 | 26.4105
Pipe-1382 | Junction-1455 | Junction-1459 | 23.23 | 0.166 | 43.1 | true | true | 172 | 0.821
Pipe-1385 | Junction-1459 | Junction-1457 | 1.59 | 0.166 | 43.1 | true | true | 172 | 0.821
Pipe-1394 | Junction-1459 | Junction-1461 | 3.53 | 0.134 | 28.5 | true | true | 60 | 0.2864
Pipe-1398 | Junction-1471 | Junction-1470 | 1.48 | 0.134 | 28.5 | true | true | 60 | 0.2864
Pipe-1400 | Junction-1472 | Junction-1473 | 6.84 | 0.585 | 28.5 | true | true | 60 | 0.2864
Pipe-1409 | Junction-1489 | Junction-1477 | 14.99 | 0.134 | 28.5 | true | true | 60 | 0.2864
Pipe-1422 | Junction-1501 | Junction-1491 | 19.51 | 0.134 | 28.5 | true | true | 60 | 0.2864
Pipe-1435 | Junction-1510 | Junction-1503 | 6.5 | 0.134 | 28.5 | true | true | 60 | 0.2864
Pipe-1437 | Junction-1503 | Junction-1512 | 5.54 | 0.156 | 28.5 | true | true | 60 | 0.2864
Pipe-1441 | Junction-1461 | Junction-1513 | 3.32 | 0.156 | 28.5 | true | true | 60 | 0.2864
Pipe-1620 | Junction-1704 | Junction-1694 | 37.86 | 0.166 | 43.1 | true | true | 172 | 0.821
Pipe-1839 | Junction-1928 | Junction-1917 | 25.27 | 0.166 | 43.1 | true | true | 172 | 0.821
Pipe-1849 | Junction-32353 | Junction-1933 | 42.36 | 0.18 | 54.5 | true | true | 321 | 1.5322
Pipe-1857 | Junction-1457 | Junction-1941 | 26.72 | 0.134 | 28.5 | true | true | 60 | 0.2864
Pipe-1867 | Junction-1501 | Junction-1471 | 34.21 | 0.166 | 43.1 | true | true | 172 | 0.821
Pipe-1875 | Junction-1510 | Junction-1501 | 1.08 | 0.166 | 43.1 | true | true | 172 | 0.821
Pipe-1876 | Junction-1489 | Junction-1510 | 1.49 | 0.166 | 43.1 | true | true | 172 | 0.821
Pipe-1880 | Junction-1475 | Junction-1489 | 2.32 | 0.166 | 43.1 | true | true | 172 | 0.821
Pipe-1881 | Junction-1455 | Junction-1471 | 6.35 | 0.166 | 43.1 | true | true | 172 | 0.821
Pipe-1911 | Junction-2006 | Junction-2007 | 0.02 | 0.282 | 160.3 | true | true | 5533 | 26.4105
Pipe-1923 | Junction-2039 | Junction-3306 | 69.22 | 0.166 | 43.1 | true | true | 172 | 0.821
Pipe-1941 | Junction-2039 | Junction-2040 | 4.82 | 0.355 | 263 | true | true | 20264 | 96.7255
Pipe-1988 | Junction-18024 | Junction-2091 | 0.47 | 0.134 | 28.5 | true | true | 60 | 0.2864
Pipe-1992 | Junction-18017 | Junction-2097 | 2.07 | 0.18 | 54.5 | true | true | 321 | 1.5322
Pipe-2003 | Junction-2103 | Junction-18033 | 5.06 | 0.282 | 160.3 | true | true | 5533 | 26.4105
Pipe-2004 | Junction-18013 | Junction-18016 | 59.9 | 0.254 | 132.5 | true | true | 3354 | 16.0095
Pipe-2017 | Junction-2140 | Junction-2042 | 33.91 | 0.18 | 54.5 | true | true | 321 | 1.5322
Pipe-2032 | Junction-2147 | Junction-2140 | 22.58 | 0.282 | 160.3 | true | true | 5533 | 26.4105
Pipe-2036 | Junction-2150 | Junction-99634 | 48.94 | 0.225 | 107.1 | true | true | 1915 | 9.1408
Pipe-2039 | Junction-2160 | Junction-2150 | 4.88 | 0.217 | 82.5 | true | true | 962 | 4.5919
Pipe-2090 | Junction-1143 | Junction-1928 | 179 | 0.205 | 70.3 | true | true | 630 | 3.0072
Pipe-2100 | Junction-5284 | Junction-1143 | 148.51 | 0.205 | 70.3 | true | true | 630 | 3.0072
Pipe-2112 | Junction-2228 | Junction-18843 | 2.39 | 0.205 | 70.3 | true | true | 630 | 3.0072
Pipe-2113 | Junction-2226 | Junction-2227 | 0.11 | 0.293 | 210.1 | true | true | 11253 | 53.7136
Pipe-2120 | Junction-2226 | Junction-2238 | 0.41 | 0.293 | 210.1 | true | true | 11253 | 53.7136
Pipe-2121 | Junction-2226 | Junction-2237 | 0.46 | 0.293 | 210.1 | true | true | 11253 | 53.7136
Pipe-2123 | Junction-2238 | Junction-15412 | 205.3 | 0.282 | 160.3 | true | true | 5533 | 26.4105
Pipe-2139 | Junction-2160 | Junction-2251 | 94.85 | 0.293 | 210.1 | true | true | 11253 | 53.7136
Pipe-2162 | Junction-2359 | Junction-2160 | 133.2 | 0.293 | 210.1 | true | true | 11253 | 53.7136
Pipe-2209 | Junction-2340 | Junction-2330 | 13.93 | 0.18 | 54.5 | true | true | 321 | 1.5322
Pipe-2227 | Junction-2251 | Junction-2360 | 3.17 | 0.85 | 210.1 | true | true | 11253 | 53.7136
Pipe-2240 | Junction-6835 | Junction-2365 | 57.21 | 0.18 | 54.5 | true | true | 321 | 1.5322
Pipe-2830 | Junction-2964 | Junction-2961 | 1.2 | 0.217 | 82.5 | true | true | 962 | 4.5919
Pipe-2927 | Junction-4719 | Junction-2964 | 1051.21 | 0.225 | 107.1 | true | true | 1915 | 9.1408
Pipe-3104 | Junction-3224 | Junction-94517 | 12.35 | 0.364 | 132.5 | true | true | 3354 | 16.0095
Pipe-3360 | Junction-3489 | Junction-3397 | 69.72 | 0.205 | 70.3 | true | true | 630 | 3.0072
Pipe-3419 | Junction-3534 | Junction-3552 | 50.66 | 0.205 | 70.3 | true | true | 630 | 3.0072
Pipe-3751 | Junction-3911 | Junction-3493 | 55.6 | 0.166 | 43.1 | true | true | 172 | 0.821
Pipe-3910 | Junction-4364 | Junction-4079 | 35.61 | 0.134 | 28.5 | true | true | 60 | 0.2864
Pipe-3944 | Junction-4122 | Junction-4108 | 51.56 | 0.166 | 43.1 | true | true | 172 | 0.821
Pipe-4553 | Junction-4720 | Junction-4719 | 2.01 | 0.282 | 160.3 | true | true | 5533 | 26.4105
Pipe-4554 | Junction-4721 | Junction-4720 | 1.42 | 0.293 | 210.1 | true | true | 11253 | 53.7136
Pipe-4555 | Junction-22540 | Junction-4721 | 2.13 | 0.355 | 263 | true | true | 20264 | 96.7255
Pipe-5091 | Junction-5297 | Junction-5284 | 48.97 | 0.205 | 70.3 | true | true | 630 | 3.0072
Pipe-5099 | Junction-5297 | Junction-2961 | 21.84 | 0.205 | 70.3 | true | true | 630 | 3.0072
Pipe-5539 | Junction-4076 | Junction-3968 | 90.09 | 0.225 | 107.1 | true | true | 1915 | 9.1408
Pipe-5789 | Junction-6013 | Junction-5699 | 102.17 | 0.18 | 54.5 | true | true | 321 | 1.5322
Pipe-5942 | Junction-6217 | Junction-5882 | 31.27 | 0.205 | 70.3 | true | true | 630 | 3.0072
Pipe-6042 | Junction-5284 | Junction-3911 | 283.14 | 0.18 | 54.5 | true | true | 321 | 1.5322
Pipe-6211 | Junction-6710 | Junction-6592 | 29.98 | 0.134 | 28.5 | true | true | 60 | 0.2864
Pipe-6355 | Junction-6643 | Junction-6583 | 22.08 | 0.166 | 43.1 | true | true | 172 | 0.821
Pipe-6393 | Junction-6630 | Junction-7838 | 103.34 | 0.166 | 43.1 | true | true | 172 | 0.821
Pipe-6483 | Junction-6592 | Junction-6712 | 9.47 | 0.156 | 28.5 | true | true | 60 | 0.2864
Pipe-6489 | Junction-6834 | Junction-6716 | 45.17 | 0.205 | 70.3 | true | true | 630 | 3.0072
Pipe-6499 | Junction-6737 | Junction-6630 | 46.86 | 0.205 | 70.3 | true | true | 630 | 3.0072
Pipe-6529 | Junction-41523 | Junction-6013 | 431.71 | 0.254 | 132.5 | true | true | 3354 | 16.0095
Pipe-6607 | Junction-6834 | Junction-6835 | 2.83 | 0.217 | 82.5 | true | true | 962 | 4.5919
Pipe-6735 | Junction-7028 | Junction-6657 | 15.17 | 0.18 | 54.5 | true | true | 321 | 1.5322
Pipe-6825 | Junction-7055 | Junction-7028 | 99.85 | 0.205 | 70.3 | true | true | 630 | 3.0072
Pipe-6930 | Junction-7161 | Junction-7150 | 12.7 | 0.166 | 43.1 | true | true | 172 | 0.821
Pipe-6998 | Junction-7222 | Junction-6487 | 48.41 | 0.205 | 70.3 | true | true | 630 | 3.0072
Pipe-7041 | Junction-7161 | Junction-19666 | 11.56 | 0.217 | 82.5 | true | true | 962 | 4.5919
Pipe-7047 | Junction-7285 | Junction-7270 | 31.47 | 0.166 | 43.1 | true | true | 172 | 0.821
Pipe-7166 | Junction-7055 | Junction-4122 | 16.9 | 0.282 | 160.3 | true | true | 5533 | 26.4105
Pipe-7218 | Junction-7443 | Junction-7442 | 12.91 | 0.225 | 107.1 | true | true | 1915 | 9.1408
Pipe-7220 | Junction-7434 | Junction-7443 | 7.16 | 0.254 | 132.5 | true | true | 3354 | 16.0095
Pipe-7271 | Junction-7518 | Junction-7055 | 302 | 0.282 | 160.3 | true | true | 5533 | 26.4105
Pipe-7335 | Junction-6013 | Junction-7434 | 434.69 | 0.254 | 132.5 | true | true | 3354 | 16.0095
Pipe-7387 | Junction-7285 | Junction-7612 | 1.48 | 0.205 | 70.3 | true | true | 630 | 3.0072
Pipe-7388 | Junction-7613 | Junction-7614 | 1.99 | 0.166 | 43.1 | true | true | 172 | 0.821
Pipe-7470 | Junction-6487 | Junction-7613 | 243.6 | 0.18 | 54.5 | true | true | 321 | 1.5322
Pipe-7570 | Junction-7795 | Junction-7883 | 763.7 | 0.293 | 210.1 | true | true | 11253 | 53.7136
Pipe-7663 | Junction-7879 | Ericsson | 127.95 | 0.293 | 210.1 | false | true | 11253 | 53.7136
Pipe-7666 | Junction-7883 | Junction-7879 | 9.37 | 0.282 | 160.3 | true | true | 5533 | 26.4105
Pipe-7923 | Junction-7434 | Junction-165 | 237.54 | 0.217 | 82.5 | true | true | 962 | 4.5919
Pipe-7927 | Junction-8165 | Junction-8150 | 12.11 | 0.166 | 43.1 | true | true | 172 | 0.821
Pipe-8800 | Junction-9062 | Junction-897 | 67.71 | 0.205 | 70.3 | true | true | 630 | 3.0072
Pipe-8865 | Junction-9115 | Junction-9041 | 22.58 | 0.436 | 160.3 | true | true | 5533 | 26.4105
Pipe-8875 | Junction-47600 | Junction-9137 | 63.22 | 0.483 | 210.1 | true | true | 11253 | 53.7136
Pipe-9213 | Junction-9252 | Junction-97934 | 96.59 | 0.37 | 210.1 | true | true | 11253 | 53.7136
Pipe-9234 | Junction-9551 | Junction-9494 | 71.16 | 0.18 | 54.5 | true | true | 321 | 1.5322
Pipe-9275 | Junction-10018 | Junction-9551 | 208.51 | 0.293 | 210.1 | true | true | 11253 | 53.7136
Pipe-9276 | Junction-9551 | Junction-99702 | 63.99 | 0.293 | 210.1 | true | true | 11253 | 53.7136
Pipe-9282 | Junction-9915 | Junction-9556 | 54.57 | 0.291 | 263 | true | true | 20264 | 96.7255
Pipe-9500 | Junction-9802 | Junction-9698 | 1.74 | 0.205 | 70.3 | true | true | 630 | 3.0072
Pipe-9501 | Junction-9802 | Junction-99110 | 33.88 | 0.282 | 160.3 | true | true | 5533 | 26.4105
Pipe-9503 | Junction-98869 | Junction-9802 | 12.42 | 0.282 | 160.3 | true | true | 5533 | 26.4105
Pipe-9505 | Junction-9808 | Junction-9809 | 0.99 | 0.254 | 132.5 | true | true | 3354 | 16.0095
Pipe-9556 | Junction-9944 | Junction-9860 | 81.85 | 0.18 | 54.5 | true | true | 321 | 1.5322
Pipe-9609 | Junction-9917 | Junction-9915 | 7.08 | 0.355 | 263 | true | true | 20264 | 96.7255
Pipe-9611 | Junction-17528 | Junction-9917 | 32.39 | 0.355 | 263 | true | true | 20264 | 96.7255
Pipe-9678 | Junction-10392 | Junction-111208 | 146.61 | 0.217 | 82.5 | true | true | 962 | 4.5919
Pipe-9713 | Junction-30414 | Junction-10018 | 58.51 | 0.293 | 210.1 | true | true | 11253 | 53.7136
Pipe-9772 | Junction-10094 | Junction-10095 | 2.19 | 0.633 | 54.5 | true | true | 321 | 1.5322
Pipe-9774 | Junction-10097 | Junction-10094 | 3.08 | 0.661 | 70.3 | true | true | 630 | 3.0072
Pipe-9776 | Junction-10097 | Junction-10099 | 2.67 | 0.661 | 70.3 | true | true | 630 | 3.0072
Pipe-9777 | Junction-10100 | Junction-10097 | 0.64 | 0.661 | 70.3 | true | true | 630 | 3.0072
Pipe-9854 | Junction-10202 | Junction-11221 | 56.39 | 0.18 | 54.5 | true | true | 321 | 1.5322
Pipe-9918 | Junction-10260 | Junction-10258 | 16.89 | 0.166 | 43.1 | true | true | 172 | 0.821
Pipe-10048 | Junction-9809 | Junction-10392 | 11.98 | 0.225 | 107.1 | true | true | 1915 | 9.1408
Pipe-10171 | Junction-10519 | Junction-10202 | 90.66 | 0.205 | 70.3 | true | true | 630 | 3.0072
Pipe-10186 | Junction-9252 | Junction-99198 | 140.91 | 0.205 | 70.3 | true | true | 630 | 3.0072
Pipe-10260 | Junction-9548 | Junction-10595 | 56.99 | 0.166 | 43.1 | true | true | 172 | 0.821
Pipe-10812 | Junction-11218 | Junction-10823 | 360.51 | 0.225 | 107.1 | true | true | 1915 | 9.1408
Pipe-10818 | Junction-11218 | Junction-43191 | 48.16 | 0.254 | 132.5 | true | true | 3354 | 16.0095
Pipe-11034 | Junction-9981 | Junction-9808 | 159.94 | 0.254 | 132.5 | true | true | 3354 | 16.0095
Pipe-11136 | Junction-11647 | Junction-9946 | 231.9 | 0.18 | 54.5 | true | true | 321 | 1.5322
Pipe-11422 | Junction-11647 | Junction-11651 | 48.76 | 0.205 | 70.3 | true | true | 630 | 3.0072
Pipe-11430 | Junction-10823 | Junction-11647 | 60.8 | 0.205 | 70.3 | true | true | 630 | 3.0072
Pipe-11515 | Junction-10823 | Junction-9944 | 88.59 | 0.225 | 107.1 | true | true | 1915 | 9.1408
Pipe-12221 | Junction-9917 | Junction-12744 | 4.93 | 0.205 | 70.3 | true | true | 630 | 3.0072
Pipe-12222 | Junction-100388 | Junction-12748 | 61.96 | 0.355 | 263 | true | true | 20264 | 96.7255
Pipe-13057 | Junction-20819 | Junction-20306 | 11.81 | 0.321 | 312.7 | true | true | 31872 | 152.1337
Pipe-13069 | Junction-98830 | Junction-13700 | 20.93 | 0.225 | 107.1 | true | true | 1915 | 9.1408
Pipe-13570 | Junction-14292 | Junction-14279 | 382.35 | 0.411 | 312.7 | true | true | 31872 | 152.1337
Pipe-13585 | Junction-47090 | Junction-48557 | 12.77 | 0.134 | 28.5 | true | true | 60 | 0.2864
Pipe-14292 | Junction-20377 | Junction-127376 | 112.73 | 0.404 | 393.8 | true | true | 58221 | 277.9045
Pipe-14312 | Junction-16220 | Junction-15021 | 19.23 | 0.18 | 54.5 | true | true | 321 | 1.5322
Pipe-14317 | Junction-13761 | Junction-13742 | 93.92 | 0.217 | 82.5 | true | true | 962 | 4.5919
Pipe-14328 | Junction-13742 | Junction-15027 | 33.03 | 0.18 | 54.5 | true | true | 321 | 1.5322
Pipe-14716 | Junction-15414 | Junction-2097 | 2.51 | 0.282 | 160.3 | true | true | 5533 | 26.4105
Pipe-14719 | Junction-18843 | Junction-2226 | 23.7 | 0.293 | 210.1 | true | true | 11253 | 53.7136
Pipe-14775 | Junction-96222 | Junction-2227 | 2.78 | 0.37 | 210.1 | true | true | 11253 | 53.7136
Pipe-14890 | Junction-15720 | Junction-16557 | 53.31 | 0.205 | 70.3 | true | true | 630 | 3.0072
Pipe-15479 | Junction-16220 | Junction-5297 | 59.28 | 0.205 | 70.3 | true | true | 630 | 3.0072
Pipe-15482 | Junction-16232 | Junction-16220 | 11.25 | 0.205 | 70.3 | true | true | 630 | 3.0072
Pipe-15492 | Junction-16338 | Junction-15720 | 338.16 | 0.217 | 82.5 | true | true | 962 | 4.5919
Pipe-15532 | Junction-16278 | Junction-16187 | 10.57 | 0.166 | 43.1 | true | true | 172 | 0.821
Pipe-15597 | Junction-16340 | Junction-16338 | 30.15 | 0.225 | 107.1 | true | true | 1915 | 9.1408
Pipe-15748 | Junction-13715 | Junction-16340 | 164.35 | 0.217 | 82.5 | true | true | 962 | 4.5919
Pipe-15855 | Junction-7612 | Junction-16605 | 31.74 | 0.166 | 43.1 | true | true | 172 | 0.821
Pipe-16026 | Junction-31545 | Junction-17137 | 39.16 | 0.18 | 54.5 | true | true | 321 | 1.5322
Pipe-16046 | Junction-17058 | Junction-16793 | 30.92 | 0.205 | 70.3 | true | true | 630 | 3.0072
Pipe-16199 | Junction-18841 | Junction-2228 | 1.71 | 0.248 | 70.3 | true | true | 630 | 3.0072
Pipe-16320 | Junction-38586 | Junction-17125 | 84.96 | 0.18 | 54.5 | true | true | 321 | 1.5322
Pipe-16354 | Junction-17173 | Junction-16837 | 67.39 | 0.18 | 54.5 | true | true | 321 | 1.5322
Pipe-16445 | Junction-18841 | Junction-18008 | 108.76 | 0.282 | 160.3 | true | true | 5533 | 26.4105
Pipe-16447 | Junction-17278 | Junction-17277 | 1.36 | 0.166 | 43.1 | true | true | 172 | 0.821
Pipe-16506 | Junction-2009 | Junction-300 | 203.81 | 0.282 | 160.3 | true | true | 5533 | 26.4105
Pipe-16512 | Junction-2007 | Junction-2009 | 1.05 | 0.282 | 160.3 | true | true | 5533 | 26.4105
Pipe-16513 | Junction-17342 | Junction-2006 | 0.14 | 0.282 | 160.3 | true | true | 5533 | 26.4105
Pipe-16606 | Junction-18873 | Junction-18874 | 45.68 | 0.18 | 54.5 | true | true | 321 | 1.5322
Pipe-16683 | Junction-12748 | Junction-17528 | 7.5 | 0.501 | 210.1 | true | true | 11253 | 53.7136
Pipe-16826 | Junction-17746 | Junction-17656 | 113.44 | 0.18 | 54.5 | true | true | 321 | 1.5322
Pipe-16909 | Junction-16565 | Junction-17746 | 28.08 | 0.205 | 70.3 | true | true | 630 | 3.0072
Pipe-17140 | Junction-17278 | Junction-2100 | 68.61 | 0.293 | 210.1 | true | true | 11253 | 53.7136
Pipe-17143 | Junction-18008 | Junction-2103 | 68.57 | 0.282 | 160.3 | true | true | 5533 | 26.4105
Pipe-17145 | Junction-18013 | Junction-2100 | 0.8 | 0.254 | 132.5 | true | true | 3354 | 16.0095
Pipe-17148 | Junction-18013 | Junction-2103 | 2.11 | 0.254 | 132.5 | true | true | 3354 | 16.0095
Pipe-17156 | Junction-2097 | Junction-18024 | 31.48 | 0.282 | 160.3 | true | true | 5533 | 26.4105
Pipe-17163 | Junction-18027 | Junction-2009 | 1.43 | 0.254 | 132.5 | true | true | 3354 | 16.0095
Pipe-17165 | Junction-18027 | Junction-2006 | 0.3 | 0.306 | 132.5 | true | true | 3354 | 16.0095
Pipe-17169 | Junction-2098 | Junction-18017 | 0.82 | 0.18 | 54.5 | true | true | 321 | 1.5322
Pipe-17863 | Junction-300 | Junction-18899 | 376.05 | 0.282 | 160.3 | true | true | 5533 | 26.4105
Pipe-17965 | Junction-18899 | Junction-18900 | 8.08 | 0.436 | 160.3 | true | true | 5533 | 26.4105
Pipe-17974 | Junction-18913 | Junction-19194 | 56.99 | 0.282 | 160.3 | true | true | 5533 | 26.4105
Pipe-17978 | Junction-18916 | Junction-18913 | 2.23 | 0.282 | 160.3 | true | true | 5533 | 26.4105
Pipe-18234 | Junction-18913 | Junction-2340 | 4.45 | 0.205 | 70.3 | true | true | 630 | 3.0072
Pipe-18239 | Junction-19191 | Junction-19185 | 7.61 | 0.205 | 70.3 | true | true | 630 | 3.0072
Pipe-18245 | Junction-19191 | Junction-19192 | 11.36 | 0.282 | 160.3 | true | true | 5533 | 26.4105
Pipe-18273 | Junction-98040 | Junction-18916 | 13.3 | 0.254 | 132.5 | true | true | 3354 | 16.0095
Pipe-18319 | Junction-19267 | Junction-19266 | 4.68 | 0.205 | 70.3 | true | true | 630 | 3.0072
Pipe-18320 | Junction-19267 | Junction-19268 | 41.34 | 0.355 | 263 | true | true | 20264 | 96.7255
Pipe-18615 | Junction-19573 | Junction-19572 | 23.06 | 0.661 | 70.3 | true | true | 630 | 3.0072
Pipe-18617 | Junction-19575 | Junction-19573 | 0.67 | 0.436 | 160.3 | true | true | 5533 | 26.4105
Pipe-18639 | Junction-7612 | Junction-21783 | 51.07 | 0.205 | 70.3 | true | true | 630 | 3.0072
Pipe-18642 | Junction-19573 | Junction-19608 | 3.86 | 0.436 | 160.3 | true | true | 5533 | 26.4105
Pipe-18645 | Junction-19612 | Junction-19611 | 23.61 | 0.213 | 54.5 | true | true | 321 | 1.5322
Pipe-18646 | Junction-19612 | Junction-19576 | 1.86 | 0.436 | 160.3 | true | true | 5533 | 26.4105
Pipe-18648 | Junction-19576 | Junction-18899 | 105.1 | 0.436 | 160.3 | true | true | 5533 | 26.4105
Pipe-18651 | Junction-18900 | Junction-19616 | 65.2 | 0.71 | 107.1 | true | true | 1915 | 9.1408
Pipe-18655 | Junction-20691 | Junction-19621 | 93.44 | 0.252 | 43.1 | true | true | 172 | 0.821
Pipe-18697 | Junction-19666 | Junction-7285 | 0.41 | 0.205 | 70.3 | true | true | 630 | 3.0072
Pipe-18725 | Junction-19699 | Junction-20761 | 83.92 | 0.321 | 312.7 | true | true | 31872 | 152.1337
Pipe-18731 | Junction-19701 | Junction-19699 | 12.17 | 0.321 | 312.7 | true | true | 31872 | 152.1337
Pipe-18854 | Junction-18873 | Junction-7518 | 2.31 | 0.355 | 263 | true | true | 20264 | 96.7255
Pipe-18941 | Junction-19916 | Junction-19911 | 3.5 | 0.18 | 54.5 | true | true | 321 | 1.5322
Pipe-19219 | Junction-20195 | Junction-20194 | 1.41 | 0.18 | 54.5 | true | true | 321 | 1.5322
Pipe-19221 | Junction-20195 | Junction-20196 | 0.51 | 0.18 | 54.5 | true | true | 321 | 1.5322
Pipe-19249 | Junction-20234 | Junction-20232 | 13.31 | 0.619 | 82.5 | true | true | 962 | 4.5919
Pipe-19251 | Junction-20234 | Junction-20236 | 11.25 | 0.619 | 82.5 | true | true | 962 | 4.5919
Pipe-19253 | Junction-20237 | Junction-20238 | 13.41 | 1 | 100 | true | true | 1915 | 9.1408
Pipe-19287 | Junction-31466 | Junction-20284 | 21.43 | 0.18 | 54.5 | true | true | 321 | 1.5322
Pipe-19295 | Junction-20306 | Junction-22022 | 79.5 | 0.225 | 107.1 | true | true | 1915 | 9.1408
Pipe-19450 | Junction-18843 | Junction-17278 | 108.69 | 0.293 | 210.1 | true | true | 11253 | 53.7136
Pipe-19454 | Junction-2100 | Junction-15414 | 4.77 | 0.293 | 210.1 | true | true | 11253 | 53.7136
Pipe-19461 | Junction-18024 | Junction-2009 | 121.78 | 0.282 | 160.3 | true | true | 5533 | 26.4105
Pipe-19465 | Junction-2237 | Junction-18841 | 23.02 | 0.282 | 160.3 | true | true | 5533 | 26.4105
Pipe-19475 | Junction-18033 | Junction-2098 | 2.26 | 0.306 | 132.5 | true | true | 3354 | 16.0095
Pipe-19478 | Junction-2098 | Junction-17342 | 152.74 | 0.306 | 132.5 | true | true | 3354 | 16.0095
Pipe-19511 | Junction-19908 | Junction-19916 | 54.83 | 0.411 | 312.7 | true | true | 31872 | 152.1337
Pipe-19665 | Junction-20230 | Junction-20234 | 65.24 | 0.71 | 107.1 | true | true | 1915 | 9.1408
Pipe-19671 | Junction-20655 | Junction-20230 | 2.92 | 0.364 | 132.5 | true | true | 3354 | 16.0095
Pipe-19674 | Junction-20656 | Junction-20659 | 5.45 | 0.71 | 107.1 | true | true | 1915 | 9.1408
Pipe-19676 | Junction-20659 | Junction-20661 | 48.38 | 1 | 100 | true | true | 1915 | 9.1408
Pipe-19679 | Junction-20663 | Junction-20664 | 0.84 | 0.483 | 210.1 | true | true | 11253 | 53.7136
Pipe-19750 | Junction-18065 | Junction-9981 | 4.08 | 0.293 | 210.1 | true | true | 11253 | 53.7136
Pipe-19752 | Junction-19575 | Junction-20655 | 77.77 | 0.364 | 132.5 | true | true | 3354 | 16.0095
Pipe-19779 | Junction-19699 | Junction-7161 | 21.37 | 0.217 | 82.5 | true | true | 962 | 4.5919
Pipe-19800 | Junction-65389 | Junction-98922 | 186.67 | 0.225 | 107.1 | true | true | 1915 | 9.1408
Pipe-19805 | Junction-20306 | Junction-19701 | 44.29 | 0.321 | 312.7 | true | true | 31872 | 152.1337
Pipe-19851 | Junction-20819 | Junction-116686 | 129.98 | 0.411 | 312.7 | true | true | 31872 | 152.1337
Pipe-20266 | Junction-21263 | Junction-21264 | 23.34 | 0.225 | 107.1 | true | true | 1915 | 9.1408
Pipe-20311 | Junction-21321 | Junction-1044 | 14.71 | 0.293 | 210.1 | true | true | 11253 | 53.7136
Pipe-20397 | Junction-38817 | Junction-21414 | 15.37 | 0.166 | 43.1 | true | true | 172 | 0.821
Pipe-20528 | Junction-19576 | Junction-21554 | 20.58 | 0.248 | 70.3 | true | true | 630 | 3.0072
Pipe-20570 | Junction-19908 | Junction-21588 | 53.11 | 0.134 | 28.5 | true | true | 60 | 0.2864
Pipe-20615 | Junction-19608 | Junction-19606 | 44.2 | 0.839 | 160.3 | true | true | 5533 | 26.4105
Pipe-20616 | Junction-19612 | Junction-19575 | 50.81 | 0.436 | 160.3 | true | true | 5533 | 26.4105
Pipe-20617 | Junction-21635 | Junction-21636 | 2.86 | 1 | 100 | true | true | 1915 | 9.1408
Pipe-20627 | Junction-21644 | Junction-3489 | 12.59 | 0.212 | 54.5 | true | true | 321 | 1.5322
Pipe-20635 | Junction-21896 | Junction-21646 | 132.72 | 0.24 | 70.3 | true | true | 630 | 3.0072
Pipe-20766 | Junction-21783 | Junction-21775 | 24.31 | 0.166 | 43.1 | true | true | 172 | 0.821
Pipe-20852 | Junction-21636 | Junction-21859 | 73.38 | 1 | 100 | true | true | 1915 | 9.1408
Pipe-20854 | Junction-20655 | Junction-21636 | 55.67 | 0.775 | 132.5 | true | true | 3354 | 16.0095
Pipe-20886 | Junction-6835 | Junction-21896 | 23.54 | 0.217 | 82.5 | true | true | 962 | 4.5919
Pipe-20890 | Junction-942 | Junction-6834 | 78.22 | 0.217 | 82.5 | true | true | 962 | 4.5919
Pipe-20978 | Junction-21644 | Junction-942 | 61.45 | 0.217 | 82.5 | true | true | 962 | 4.5919
Pipe-21037 | Junction-20664 | Junction-22041 | 5.32 | 0.633 | 54.5 | true | true | 321 | 1.5322
Pipe-21038 | Junction-20664 | Junction-19606 | 40.92 | 0.483 | 210.1 | true | true | 11253 | 53.7136
Pipe-21042 | Junction-20656 | Junction-22045 | 48.74 | 0.71 | 107.1 | true | true | 1915 | 9.1408
Pipe-21177 | Junction-22175 | Junction-36301 | 6.3 | 0.282 | 160.3 | true | true | 5533 | 26.4105
Pipe-21280 | Junction-23339 | Junction-22540 | 2090.23 | 0.355 | 263 | true | true | 20264 | 96.7255
Pipe-21882 | Junction-22045 | Junction-20653 | 15.11 | 0.71 | 107.1 | true | true | 1915 | 9.1408
Pipe-21884 | Junction-22045 | Junction-22905 | 32.27 | 1 | 100 | true | true | 1915 | 9.1408
Pipe-21888 | Junction-22039 | Junction-20237 | 147.32 | 0.364 | 132.5 | true | true | 3354 | 16.0095
Pipe-21889 | Junction-20663 | Junction-22039 | 0.28 | 0.839 | 160.3 | true | true | 5533 | 26.4105
Pipe-21896 | Junction-22919 | Junction-22908 | 50.23 | 0.18 | 54.5 | true | true | 321 | 1.5322
Pipe-21987 | Junction-21263 | Junction-23009 | 61.86 | 0.166 | 43.1 | true | true | 172 | 0.821
Pipe-22270 | Junction-22540 | Junction-23337 | 585.98 | 0.282 | 160.3 | true | true | 5533 | 26.4105
Pipe-22630 | Junction-21265 | Junction-23720 | 43.86 | 0.18 | 54.5 | true | true | 321 | 1.5322
Pipe-23791 | Junction-26246 | Junction-24920 | 11.23 | 0.166 | 43.1 | true | true | 172 | 0.821
Pipe-24171 | Junction-25543 | Junction-25321 | 11.27 | 0.18 | 54.5 | true | true | 321 | 1.5322
Pipe-24327 | Junction-25486 | Junction-25472 | 28.05 | 0.166 | 43.1 | true | true | 172 | 0.821
Pipe-24334 | Junction-25486 | Junction-31990 | 36.62 | 0.355 | 263 | true | true | 20264 | 96.7255
Pipe-25111 | Junction-27498 | Junction-26248 | 178.17 | 0.293 | 210.1 | true | true | 11253 | 53.7136
Pipe-25643 | Junction-18021 | Junction-2091 | 1.76 | 0.134 | 28.5 | true | true | 60 | 0.2864
Pipe-25785 | Junction-32586 | Junction-26998 | 34.64 | 0.213 | 54.5 | true | true | 321 | 1.5322
Pipe-25812 | Junction-26973 | Junction-27615 | 29.28 | 0.18 | 54.5 | true | true | 321 | 1.5322
Pipe-25835 | Junction-26996 | Junction-26989 | 20 | 0.18 | 54.5 | true | true | 321 | 1.5322
Pipe-26084 | Junction-27084 | Junction-27239 | 38.7 | 0.18 | 54.5 | true | true | 321 | 1.5322
Pipe-27646 | Junction-29936 | Junction-14292 | 159.97 | 0.293 | 210.1 | true | true | 11253 | 53.7136
Pipe-27660 | Junction-28458 | Junction-29012 | 55.31 | 0.166 | 43.1 | true | true | 172 | 0.821
Pipe-27993 | Junction-28458 | Junction-29352 | 122.78 | 0.225 | 107.1 | true | true | 1915 | 9.1408
Pipe-28121 | Junction-2091 | Junction-29484 | 33.45 | 0.134 | 28.5 | true | true | 60 | 0.2864
Pipe-28243 | Junction-29632 | Junction-29629 | 10.92 | 0.225 | 107.1 | true | true | 1915 | 9.1408
Pipe-28244 | Junction-29632 | Junction-25486 | 3.47 | 0.355 | 263 | true | true | 20264 | 96.7255
Pipe-28337 | Junction-28618 | Junction-25489 | 35.65 | 0.18 | 54.5 | true | true | 321 | 1.5322
Pipe-28468 | Junction-29873 | Junction-29864 | 32.15 | 0.134 | 28.5 | true | true | 60 | 0.2864
Pipe-28537 | Junction-29352 | Junction-29939 | 31.54 | 0.166 | 43.1 | true | true | 172 | 0.821
Pipe-28590 | Junction-30008 | Junction-29994 | 124.58 | 0.205 | 70.3 | true | true | 630 | 3.0072
Pipe-29139 | Junction-30728 | Junction-30575 | 74.52 | 0.187 | 43.1 | true | true | 172 | 0.821
Pipe-29516 | Junction-18017 | Junction-20195 | 32.61 | 0.18 | 54.5 | true | true | 321 | 1.5322
Pipe-29989 | Junction-22919 | Junction-31466 | 32.3 | 0.205 | 70.3 | true | true | 630 | 3.0072
Pipe-30047 | Junction-31788 | Junction-31545 | 18.81 | 0.205 | 70.3 | true | true | 630 | 3.0072
Pipe-30141 | Junction-31656 | Junction-31469 | 81.83 | 0.205 | 70.3 | true | true | 630 | 3.0072
Pipe-30272 | Junction-32382 | Junction-31788 | 27.01 | 0.205 | 70.3 | true | true | 630 | 3.0072
Pipe-30379 | Junction-31915 | Junction-33148 | 60.03 | 0.321 | 312.7 | true | true | 31872 | 152.1337
Pipe-30400 | Junction-19701 | Junction-32090 | 18.63 | 0.166 | 43.1 | true | true | 172 | 0.821
Pipe-30458 | Junction-31990 | Junction-31937 | 16.42 | 0.166 | 43.1 | true | true | 172 | 0.821
Pipe-30802 | Junction-31469 | Junction-32344 | 21.71 | 0.18 | 54.5 | true | true | 321 | 1.5322
Pipe-30806 | Junction-32355 | Junction-32353 | 27.56 | 0.205 | 70.3 | true | true | 630 | 3.0072
Pipe-30831 | Junction-31469 | Junction-22919 | 1.87 | 0.205 | 70.3 | true | true | 630 | 3.0072
Pipe-30834 | Junction-31466 | Junction-32382 | 12.43 | 0.205 | 70.3 | true | true | 630 | 3.0072
Pipe-30835 | Junction-6643 | Junction-32382 | 34.01 | 0.18 | 54.5 | true | true | 321 | 1.5322
Pipe-30848 | Junction-31545 | Junction-32358 | 66.08 | 0.205 | 70.3 | true | true | 630 | 3.0072
Pipe-30969 | Junction-9137 | Junction-32355 | 59.54 | 0.205 | 70.3 | true | true | 630 | 3.0072
Pipe-31011 | Junction-31788 | Junction-19740 | 106.04 | 0.18 | 54.5 | true | true | 321 | 1.5322
Pipe-31020 | Junction-32591 | Junction-1398 | 67.57 | 0.18 | 54.5 | true | true | 321 | 1.5322
Pipe-31093 | Junction-32355 | Junction-10260 | 12.21 | 0.18 | 54.5 | true | true | 321 | 1.5322
Pipe-31130 | Junction-32358 | Junction-32586 | 20.93 | 0.205 | 70.3 | true | true | 630 | 3.0072
Pipe-31135 | Junction-32591 | Junction-32358 | 2.94 | 0.205 | 70.3 | true | true | 630 | 3.0072
Pipe-31136 | Junction-32703 | Junction-32591 | 20.79 | 0.205 | 70.3 | true | true | 630 | 3.0072
Pipe-31362 | Junction-32353 | Junction-32703 | 70.51 | 0.205 | 70.3 | true | true | 630 | 3.0072
Pipe-31397 | Junction-31657 | Junction-34250 | 100.54 | 0.166 | 43.1 | true | true | 172 | 0.821
Pipe-31699 | Junction-36047 | Junction-99781 | 80.32 | 0.205 | 70.3 | true | true | 630 | 3.0072
Pipe-31831 | Junction-33431 | Junction-33432 | 20.04 | 0.355 | 263 | true | true | 20264 | 96.7255
Pipe-32202 | Junction-16232 | Junction-33839 | 121.17 | 0.18 | 54.5 | true | true | 321 | 1.5322
Pipe-32205 | Junction-33847 | Junction-33846 | 3 | 0.18 | 54.5 | true | true | 321 | 1.5322
Pipe-32276 | Junction-32703 | Junction-33920 | 6.16 | 0.134 | 28.5 | true | true | 60 | 0.2864
Pipe-32310 | Junction-33957 | Junction-33952 | 36.64 | 0.166 | 43.1 | true | true | 172 | 0.821
Pipe-32330 | Junction-32340 | Junction-32341 | 26.21 | 0.225 | 107.1 | true | true | 1915 | 9.1408
Pipe-32381 | Junction-26248 | Junction-122930 | 203.51 | 0.355 | 263 | true | true | 20264 | 96.7255
Pipe-32410 | Junction-33846 | Junction-34066 | 49.83 | 0.259 | 82.5 | true | true | 962 | 4.5919
Pipe-32411 | Junction-33847 | Junction-34067 | 9.55 | 0.213 | 54.5 | true | true | 321 | 1.5322
Pipe-32492 | Junction-34156 | Junction-34155 | 13.08 | 0.18 | 54.5 | true | true | 321 | 1.5322
Pipe-32494 | Junction-21264 | Junction-34156 | 20.92 | 0.217 | 82.5 | true | true | 962 | 4.5919
Pipe-32524 | Junction-34547 | Junction-34191 | 4.39 | 0.217 | 82.5 | true | true | 962 | 4.5919
Pipe-32582 | Junction-34248 | Junction-32957 | 26.69 | 0.134 | 28.5 | true | true | 60 | 0.2864
Pipe-32795 | Junction-34444 | Junction-22175 | 127.1 | 0.282 | 160.3 | true | true | 5533 | 26.4105
Pipe-33568 | Junction-34334 | Junction-35245 | 22.49 | 0.134 | 28.5 | true | true | 60 | 0.2864
Pipe-33884 | Junction-33431 | Junction-36767 | 1344.46 | 0.293 | 210.1 | true | true | 11253 | 53.7136
Pipe-34012 | Junction-27498 | Junction-35697 | 3.93 | 0.217 | 82.5 | true | true | 962 | 4.5919
Pipe-34064 | Junction-34444 | Junction-36476 | 239.89 | 0.411 | 312.7 | true | true | 31872 | 152.1337
Pipe-34102 | Junction-35794 | Junction-35793 | 18.55 | 0.166 | 43.1 | true | true | 172 | 0.821
Pipe-34319 | Junction-37011 | Junction-36016 | 11.6 | 0.134 | 28.5 | true | true | 60 | 0.2864
Pipe-34495 | Junction-21265 | Junction-26248 | 38.11 | 0.355 | 263 | true | true | 20264 | 96.7255
Pipe-34498 | Junction-25543 | Junction-21265 | 158.69 | 0.355 | 263 | true | true | 20264 | 96.7255
Pipe-34567 | Junction-17173 | Junction-27501 | 33.99 | 0.217 | 82.5 | true | true | 962 | 4.5919
Pipe-34569 | Junction-36258 | Junction-17173 | 8.92 | 0.217 | 82.5 | true | true | 962 | 4.5919
Pipe-35060 | Junction-36767 | Junction-23339 | 0.52 | 0.293 | 210.1 | true | true | 11253 | 53.7136
Pipe-35062 | Junction-35871 | Junction-36767 | 19.69 | 0.282 | 160.3 | true | true | 5533 | 26.4105
Pipe-35066 | Junction-35697 | Junction-36773 | 11.07 | 0.293 | 210.1 | true | true | 11253 | 53.7136
Pipe-35241 | Junction-39409 | Junction-36958 | 42.71 | 0.18 | 54.5 | true | true | 321 | 1.5322
Pipe-35246 | Junction-61767 | Junction-36967 | 19.52 | 0.18 | 54.5 | true | true | 321 | 1.5322
Pipe-35572 | Junction-37316 | Junction-29632 | 42.5 | 0.355 | 263 | true | true | 20264 | 96.7255
Pipe-35575 | Junction-36476 | Junction-37316 | 36.5 | 0.355 | 263 | true | true | 20264 | 96.7255
Pipe-35616 | Junction-37605 | Junction-37396 | 19.22 | 0.254 | 132.5 | true | true | 3354 | 16.0095
Pipe-35779 | Junction-70718 | Junction-37764 | 23.23 | 0.217 | 82.5 | true | true | 962 | 4.5919
Pipe-35780 | Junction-64275 | Junction-37544 | 23.16 | 0.205 | 70.3 | true | true | 630 | 3.0072
Pipe-35828 | Junction-37596 | Junction-37591 | 25.28 | 0.166 | 43.1 | true | true | 172 | 0.821
Pipe-35831 | Junction-37303 | Junction-37299 | 21.68 | 0.254 | 132.5 | true | true | 3354 | 16.0095
Pipe-35832 | Junction-36471 | Junction-35871 | 2.13 | 0.254 | 132.5 | true | true | 3354 | 16.0095
Pipe-35834 | Junction-34334 | Junction-34248 | 72.36 | 0.205 | 70.3 | true | true | 630 | 3.0072
Pipe-35841 | Junction-39122 | Junction-37605 | 97.15 | 0.205 | 70.3 | true | true | 630 | 3.0072
Pipe-35956 | Junction-39145 | Junction-37727 | 33.97 | 0.205 | 70.3 | true | true | 630 | 3.0072
Pipe-35962 | Junction-37727 | Junction-37731 | 78.73 | 0.205 | 70.3 | true | true | 630 | 3.0072
Pipe-36012 | Junction-36968 | Junction-37782 | 8.31 | 0.134 | 28.5 | true | true | 60 | 0.2864
Pipe-36069 | Junction-37844 | Junction-35697 | 77.72 | 0.293 | 210.1 | true | true | 11253 | 53.7136
Pipe-36070 | Junction-37844 | Junction-37845 | 2.16 | 0.282 | 160.3 | true | true | 5533 | 26.4105
Pipe-36112 | Junction-37885 | Junction-37884 | 8.72 | 0.18 | 54.5 | true | true | 321 | 1.5322
Pipe-36166 | Junction-37299 | Junction-37788 | 126.92 | 0.254 | 132.5 | true | true | 3354 | 16.0095
Pipe-36241 | Junction-38006 | Junction-37303 | 27.34 | 0.254 | 132.5 | true | true | 3354 | 16.0095
Pipe-36299 | Junction-37885 | Junction-100318 | 11.98 | 0.225 | 107.1 | true | true | 1915 | 9.1408
Pipe-36400 | Junction-65528 | Junction-99111 | 350.24 | 0.254 | 132.5 | true | true | 3354 | 16.0095
Pipe-36472 | Junction-38294 | Junction-38245 | 337.72 | 0.205 | 70.3 | true | true | 630 | 3.0072
Pipe-36568 | Junction-38425 | Junction-38343 | 25.4 | 0.134 | 28.5 | true | true | 60 | 0.2864
Pipe-36573 | Junction-49268 | Junction-68862 | 32.55 | 0.205 | 70.3 | true | true | 630 | 3.0072
Pipe-36575 | Junction-38356 | Junction-38353 | 23.28 | 0.205 | 70.3 | true | true | 630 | 3.0072
Pipe-36643 | Junction-37731 | Junction-38427 | 1.26 | 0.18 | 54.5 | true | true | 321 | 1.5322
Pipe-36647 | Junction-37727 | Junction-38429 | 70.73 | 0.18 | 54.5 | true | true | 321 | 1.5322
Pipe-36662 | Junction-68862 | Junction-38449 | 11.25 | 0.18 | 54.5 | true | true | 321 | 1.5322
Pipe-36667 | Junction-38460 | Junction-64665 | 9.34 | 0.166 | 43.1 | true | true | 172 | 0.821
Pipe-36669 | Junction-38463 | Junction-38460 | 8.54 | 0.166 | 43.1 | true | true | 172 | 0.821
Pipe-36785 | Junction-38586 | Junction-39113 | 58.53 | 0.18 | 54.5 | true | true | 321 | 1.5322
Pipe-36794 | Junction-38245 | Junction-38595 | 11.54 | 0.18 | 54.5 | true | true | 321 | 1.5322
Pipe-36848 | Junction-38805 | Junction-38652 | 79.88 | 0.205 | 70.3 | true | true | 630 | 3.0072
Pipe-36850 | Junction-53615 | Junction-46680 | 181.71 | 0.254 | 132.5 | true | true | 3354 | 16.0095
Pipe-36964 | Junction-38786 | Junction-58780 | 24.27 | 0.205 | 70.3 | true | true | 630 | 3.0072
Pipe-36965 | Junction-38803 | Junction-38786 | 10.9 | 0.217 | 82.5 | true | true | 962 | 4.5919
Pipe-36977 | Junction-38492 | Junction-38803 | 15.43 | 0.217 | 82.5 | true | true | 962 | 4.5919
Pipe-36984 | Junction-38817 | Junction-47050 | 27.79 | 0.18 | 54.5 | true | true | 321 | 1.5322
Pipe-36988 | Junction-38449 | Junction-38817 | 101.12 | 0.18 | 54.5 | true | true | 321 | 1.5322
Pipe-37065 | Junction-63624 | Junction-38905 | 12.2 | 0.134 | 28.5 | true | true | 60 | 0.2864
Pipe-37184 | Junction-17656 | Junction-39039 | 65.09 | 0.166 | 43.1 | true | true | 172 | 0.821
Pipe-37198 | Junction-39059 | Junction-53615 | 41.95 | 0.217 | 82.5 | true | true | 962 | 4.5919
Pipe-37205 | Junction-39122 | Junction-39069 | 55.56 | 0.217 | 82.5 | true | true | 962 | 4.5919
Pipe-37283 | Junction-39145 | Junction-48934 | 16.98 | 0.205 | 70.3 | true | true | 630 | 3.0072
Pipe-37284 | Junction-99277 | Junction-98936 | 87.15 | 0.254 | 132.5 | true | true | 3354 | 16.0095
Pipe-37285 | Junction-39152 | Junction-39150 | 5.55 | 0.191 | 43.1 | true | true | 172 | 0.821
Pipe-37374 | Junction-36469 | Junction-36471 | 65.09 | 0.282 | 160.3 | true | true | 5533 | 26.4105
Pipe-37508 | Junction-36951 | Junction-36968 | 60.24 | 0.18 | 54.5 | true | true | 321 | 1.5322
Pipe-37834 | Junction-36469 | Junction-39721 | 106.61 | 0.254 | 132.5 | true | true | 3354 | 16.0095
Pipe-38016 | Junction-26973 | Junction-17058 | 154.64 | 0.217 | 82.5 | true | true | 962 | 4.5919
Pipe-38422 | Junction-41132 | Junction-26973 | 99.14 | 0.217 | 82.5 | true | true | 962 | 4.5919
Pipe-38461 | Junction-40767 | Junction-41095 | 45.99 | 0.134 | 28.5 | true | true | 60 | 0.2864
Pipe-38603 | Junction-34033 | Junction-19267 | 240.13 | 0.355 | 263 | true | true | 20264 | 96.7255
Pipe-38720 | Junction-40791 | Junction-40770 | 34.57 | 0.134 | 28.5 | true | true | 60 | 0.2864
Pipe-38741 | Junction-39721 | Junction-40794 | 24.27 | 0.134 | 28.5 | true | true | 60 | 0.2864
Pipe-38896 | Junction-40961 | Junction-97997 | 48.56 | 0.166 | 43.1 | true | true | 172 | 0.821
Pipe-38938 | Junction-41008 | Junction-99525 | 28.08 | 0.217 | 82.5 | true | true | 962 | 4.5919
Pipe-38964 | Junction-36047 | Junction-41031 | 8.23 | 0.205 | 70.3 | true | true | 630 | 3.0072
Pipe-38965 | Junction-36047 | Junction-41026 | 73.06 | 0.217 | 82.5 | true | true | 962 | 4.5919
Pipe-38991 | Junction-41058 | Junction-41049 | 9.05 | 0.166 | 43.1 | true | true | 172 | 0.821
Pipe-39019 | Junction-41082 | Junction-40892 | 44.58 | 0.18 | 54.5 | true | true | 321 | 1.5322
Pipe-39046 | Junction-39721 | Junction-39719 | 11.78 | 0.254 | 132.5 | true | true | 3354 | 16.0095
Pipe-39048 | Junction-38006 | Junction-41107 | 17.03 | 0.134 | 28.5 | true | true | 60 | 0.2864
Pipe-39154 | Junction-39719 | Junction-38006 | 29.93 | 0.254 | 132.5 | true | true | 3354 | 16.0095
Pipe-39253 | Junction-40889 | Junction-41060 | 180.66 | 0.254 | 132.5 | true | true | 3354 | 16.0095
Pipe-39379 | Junction-41740 | Junction-41266 | 91.25 | 0.18 | 54.5 | true | true | 321 | 1.5322
Pipe-39463 | Junction-41442 | Junction-41523 | 52.74 | 0.254 | 132.5 | true | true | 3354 | 16.0095
Pipe-39505 | Junction-41577 | Junction-41572 | 7.74 | 0.205 | 70.3 | true | true | 630 | 3.0072
Pipe-39508 | Junction-41582 | Junction-41577 | 62.4 | 0.205 | 70.3 | true | true | 630 | 3.0072
Pipe-39513 | Junction-41740 | Junction-41582 | 5.3 | 0.217 | 82.5 | true | true | 962 | 4.5919
Pipe-39518 | Junction-41587 | Junction-18873 | 19 | 0.355 | 263 | true | true | 20264 | 96.7255
Pipe-39519 | Junction-41683 | Junction-41587 | 90.91 | 0.355 | 263 | true | true | 20264 | 96.7255
Pipe-39539 | Junction-41619 | Junction-41711 | 23.64 | 0.18 | 54.5 | true | true | 321 | 1.5322
Pipe-39558 | Junction-41620 | Junction-41619 | 14 | 0.633 | 54.5 | true | true | 321 | 1.5322
Pipe-39561 | Junction-42099 | Junction-10100 | 72.39 | 0.205 | 70.3 | true | true | 630 | 3.0072
Pipe-39598 | Junction-41572 | Kummihovi_EMP | 81.23 | 0.18 | 54.5 | true | true | 321 | 1.5322
Pipe-39618 | Junction-23337 | Junction-41683 | 1.37 | 0.355 | 263 | true | true | 20264 | 96.7255
Pipe-39647 | Junction-39719 | Junction-41716 | 53.86 | 0.18 | 54.5 | true | true | 321 | 1.5322
Pipe-39673 | Junction-41683 | Junction-41740 | 70.91 | 0.217 | 82.5 | true | true | 962 | 4.5919
Pipe-39760 | Junction-37316 | Junction-41940 | 37.11 | 0.166 | 43.1 | true | true | 172 | 0.821
Pipe-39812 | Kantvik_EMP | Junction-41587 | 81.76 | 0.18 | 54.5 | true | true | 321 | 1.5322
Pipe-40036 | Junction-41523 | Junction-42099 | 66.25 | 0.217 | 82.5 | true | true | 962 | 4.5919
Pipe-40218 | Junction-39156 | Junction-64013 | 21.64 | 0.254 | 132.5 | true | true | 3354 | 16.0095
Pipe-40225 | Junction-42312 | Junction-42178 | 45.12 | 1 | 100 | true | true | 1915 | 9.1408
Pipe-40267 | Junction-41026 | Junction-36258 | 4.16 | 0.248 | 70.3 | true | true | 630 | 3.0072
Pipe-40559 | Junction-37299 | Junction-42763 | 19.59 | 1 | 100 | true | true | 1915 | 9.1408
Pipe-40583 | Junction-41026 | Junction-27498 | 151.88 | 0.217 | 82.5 | true | true | 962 | 4.5919
Pipe-40611 | Junction-41577 | Junction-42686 | 11.95 | 1 | 100 | true | true | 1915 | 9.1408
Pipe-40625 | Junction-39156 | Junction-42748 | 31.72 | 0.18 | 54.5 | true | true | 321 | 1.5322
Pipe-40637 | Junction-42312 | Junction-42761 | 5.52 | 0.18 | 54.5 | true | true | 321 | 1.5322
Pipe-41034 | Junction-41082 | Junction-11218 | 51.58 | 0.254 | 132.5 | true | true | 3354 | 16.0095
Pipe-41403 | Junction-43566 | Junction-43562 | 21.12 | 0.134 | 28.5 | true | true | 60 | 0.2864
Pipe-41445 | Junction-42407 | Junction-43595 | 50.08 | 0.205 | 70.3 | true | true | 630 | 3.0072
Pipe-41665 | Junction-42407 | Junction-41442 | 40.94 | 0.411 | 312.7 | true | true | 31872 | 152.1337
Pipe-42448 | Junction-43191 | Junction-44635 | 35.52 | 0.18 | 54.5 | true | true | 321 | 1.5322
Pipe-42741 | Junction-35760 | Junction-44920 | 17.86 | 1 | 100 | true | true | 1915 | 9.1408
Pipe-43159 | Junction-14261 | Junction-33148 | 364.07 | 0.411 | 312.7 | true | true | 31872 | 152.1337
Pipe-43542 | Junction-99889 | Junction-45717 | 20.93 | 0.217 | 82.5 | true | true | 962 | 4.5919
Pipe-43724 | Junction-45888 | Junction-45254 | 61.72 | 0.134 | 28.5 | true | true | 60 | 0.2864
Pipe-43730 | Junction-45888 | Junction-60532 | 2.41 | 0.18 | 54.5 | true | true | 321 | 1.5322
Pipe-43755 | Junction-31915 | Junction-42407 | 1604.28 | 0.411 | 312.7 | true | true | 31872 | 152.1337
Pipe-43821 | Junction-50543 | Junction-45979 | 56.99 | 0.166 | 43.1 | true | true | 172 | 0.821
Pipe-43946 | Junction-46121 | Junction-43566 | 20.21 | 0.18 | 54.5 | true | true | 321 | 1.5322
Pipe-44023 | Junction-46214 | Junction-46212 | 9.85 | 0.134 | 28.5 | true | true | 60 | 0.2864
Pipe-44030 | Junction-46223 | Junction-46217 | 31.09 | 0.134 | 28.5 | true | true | 60 | 0.2864
Pipe-44034 | Junction-46849 | Junction-46225 | 23.95 | 0.134 | 28.5 | true | true | 60 | 0.2864
Pipe-44037 | Junction-46223 | Junction-46228 | 7.14 | 0.18 | 54.5 | true | true | 321 | 1.5322
Pipe-44108 | Junction-46121 | Junction-49563 | 6.76 | 0.134 | 28.5 | true | true | 60 | 0.2864
Pipe-44348 | Junction-84173 | Junction-46597 | 88.68 | 0.18 | 54.5 | true | true | 321 | 1.5322
Pipe-44646 | Junction-46228 | Junction-46923 | 8.45 | 0.18 | 54.5 | true | true | 321 | 1.5322
Pipe-44763 | Junction-47050 | Junction-47051 | 3.65 | 0.18 | 54.5 | true | true | 321 | 1.5322
Pipe-44916 | Junction-46131 | Junction-47223 | 19.36 | 0.18 | 54.5 | true | true | 321 | 1.5322
Pipe-45222 | Junction-47600 | Junction-46131 | 350.11 | 0.411 | 312.7 | true | true | 31872 | 152.1337
Pipe-45240 | Junction-21264 | Junction-47603 | 24.93 | 0.18 | 54.5 | true | true | 321 | 1.5322
Pipe-45242 | Junction-48555 | Junction-21263 | 72.61 | 0.225 | 107.1 | true | true | 1915 | 9.1408
Pipe-45486 | Junction-47852 | Junction-47851 | 5.54 | 0.134 | 28.5 | true | true | 60 | 0.2864
Pipe-45487 | Junction-47852 | Junction-49026 | 36.58 | 0.225 | 107.1 | true | true | 1915 | 9.1408
Pipe-45492 | Junction-46228 | Junction-47855 | 42.33 | 0.134 | 28.5 | true | true | 60 | 0.2864
Pipe-45532 | Junction-53612 | Junction-47904 | 217.55 | 0.254 | 132.5 | true | true | 3354 | 16.0095
Pipe-45553 | Junction-47934 | Junction-49938 | 6.08 | 0.18 | 54.5 | true | true | 321 | 1.5322
Pipe-45554 | Junction-47936 | Junction-47934 | 4.98 | 0.18 | 54.5 | true | true | 321 | 1.5322
Pipe-45595 | Junction-49052 | Junction-47093 | 26.46 | 0.134 | 28.5 | true | true | 60 | 0.2864
Pipe-45661 | Junction-52254 | Junction-47936 | 44.1 | 0.18 | 54.5 | true | true | 321 | 1.5322
Pipe-45721 | Junction-47088 | Junction-46129 | 14.33 | 0.18 | 54.5 | true | true | 321 | 1.5322
Pipe-45736 | Junction-64662 | Junction-48140 | 46.66 | 0.225 | 107.1 | true | true | 1915 | 9.1408
Pipe-45739 | Junction-46680 | Neidonkallio_EMP_2 | 77.86 | 0.166 | 43.1 | true | true | 172 | 0.821
Pipe-45859 | Junction-47050 | Junction-48274 | 81.64 | 0.18 | 54.5 | true | true | 321 | 1.5322
Pipe-45904 | Junction-46680 | Junction-37605 | 17.28 | 0.254 | 132.5 | true | true | 3354 | 16.0095
Pipe-45906 | Junction-48315 | Junction-48312 | 21.34 | 0.134 | 28.5 | true | true | 60 | 0.2864
Pipe-45913 | Junction-48324 | Junction-48318 | 25.93 | 0.134 | 28.5 | true | true | 60 | 0.2864
Pipe-45917 | Junction-48324 | Junction-51044 | 40.63 | 0.225 | 107.1 | true | true | 1915 | 9.1408
Pipe-45974 | Junction-48140 | Junction-48626 | 47.09 | 0.166 | 43.1 | true | true | 172 | 0.821
Pipe-46210 | Junction-38425 | Junction-39145 | 86.78 | 0.205 | 70.3 | true | true | 630 | 3.0072
Pipe-46544 | Junction-46849 | Junction-49024 | 17.21 | 0.225 | 107.1 | true | true | 1915 | 9.1408
Pipe-46546 | Junction-49026 | Junction-46849 | 11.82 | 0.225 | 107.1 | true | true | 1915 | 9.1408
Pipe-46644 | Junction-49142 | Junction-49141 | 6.21 | 0.134 | 28.5 | true | true | 60 | 0.2864
Pipe-46753 | Junction-48274 | Junction-49267 | 6.33 | 0.166 | 43.1 | true | true | 172 | 0.821
Pipe-46756 | Junction-38353 | Junction-49268 | 0.87 | 0.205 | 70.3 | true | true | 630 | 3.0072
Pipe-46870 | Junction-49142 | Junction-13761 | 320.36 | 0.225 | 107.1 | true | true | 1915 | 9.1408
Pipe-46887 | Junction-49052 | Junction-49413 | 1.37 | 0.18 | 54.5 | true | true | 321 | 1.5322
Pipe-47053 | Junction-49604 | Junction-49052 | 55.17 | 0.18 | 54.5 | true | true | 321 | 1.5322
Pipe-47193 | Junction-49757 | Junction-49754 | 26.64 | 0.18 | 54.5 | true | true | 321 | 1.5322
Pipe-47195 | Junction-49413 | Junction-49757 | 10.15 | 0.18 | 54.5 | true | true | 321 | 1.5322
Pipe-47233 | Junction-38353 | Junction-49794 | 34.11 | 0.166 | 43.1 | true | true | 172 | 0.821
Pipe-47356 | Junction-49938 | Junction-49415 | 19.51 | 0.134 | 28.5 | true | true | 60 | 0.2864
Pipe-47361 | Junction-49938 | Junction-29873 | 3 | 0.18 | 54.5 | true | true | 321 | 1.5322
Pipe-47431 | Junction-50025 | Junction-52026 | 33.18 | 0.134 | 28.5 | true | true | 60 | 0.2864
Pipe-47438 | Junction-14279 | Junction-50028 | 84.2 | 0.18 | 54.5 | true | true | 321 | 1.5322
Pipe-47592 | Junction-49757 | Junction-50187 | 20.52 | 0.134 | 28.5 | true | true | 60 | 0.2864
Pipe-47633 | Junction-49190 | Junction-41058 | 50.65 | 0.217 | 82.5 | true | true | 962 | 4.5919
Pipe-47668 | Junction-41058 | Junction-50272 | 178.57 | 0.217 | 82.5 | true | true | 962 | 4.5919
Pipe-47696 | Junction-51044 | Junction-50299 | 30.6 | 0.134 | 28.5 | true | true | 60 | 0.2864
Pipe-47726 | Junction-49024 | Junction-50328 | 19.04 | 0.134 | 28.5 | true | true | 60 | 0.2864
Pipe-47796 | Junction-47904 | Junction-52874 | 37.16 | 0.134 | 28.5 | true | true | 60 | 0.2864
Pipe-47798 | Junction-47904 | Junction-50404 | 60.43 | 0.254 | 132.5 | true | true | 3354 | 16.0095
Pipe-47854 | Junction-49413 | Junction-50461 | 17.67 | 0.134 | 28.5 | true | true | 60 | 0.2864
Pipe-47857 | Junction-46214 | Junction-46223 | 10.63 | 0.18 | 54.5 | true | true | 321 | 1.5322
Pipe-48054 | Junction-50272 | Junction-52417 | 56.12 | 0.166 | 43.1 | true | true | 172 | 0.821
Pipe-48069 | Junction-46923 | Junction-50652 | 9.3 | 0.134 | 28.5 | true | true | 60 | 0.2864
Pipe-48105 | Junction-49604 | Junction-49142 | 18.3 | 0.225 | 107.1 | true | true | 1915 | 9.1408
Pipe-48110 | Junction-50999 | Junction-49604 | 71.68 | 0.225 | 107.1 | true | true | 1915 | 9.1408
Pipe-48111 | Junction-48688 | Junction-50999 | 25.8 | 0.225 | 107.1 | true | true | 1915 | 9.1408
Pipe-48113 | Junction-28618 | Junction-102036 | 37.28 | 0.225 | 107.1 | true | true | 1915 | 9.1408
Pipe-48203 | Junction-50787 | Junction-50786 | 8.53 | 0.166 | 43.1 | true | true | 172 | 0.821
Pipe-48205 | Junction-6217 | Junction-50787 | 60.61 | 0.225 | 107.1 | true | true | 1915 | 9.1408
Pipe-48373 | Junction-38449 | Junction-50972 | 45.64 | 0.166 | 43.1 | true | true | 172 | 0.821
Pipe-48427 | Junction-51026 | Junction-38294 | 50.47 | 0.225 | 107.1 | true | true | 1915 | 9.1408
Pipe-48430 | Junction-49024 | Junction-48324 | 41.27 | 0.225 | 107.1 | true | true | 1915 | 9.1408
Pipe-48441 | Junction-50025 | Junction-28618 | 42.33 | 0.225 | 107.1 | true | true | 1915 | 9.1408
Pipe-48544 | Junction-26996 | Junction-51163 | 13.19 | 0.134 | 28.5 | true | true | 60 | 0.2864
Pipe-48761 | Junction-50999 | Junction-26996 | 46.3 | 0.18 | 54.5 | true | true | 321 | 1.5322
Pipe-48847 | Junction-52889 | Junction-51508 | 43.83 | 0.166 | 43.1 | true | true | 172 | 0.821
Pipe-48875 | Junction-51524 | Junction-6217 | 42.79 | 0.225 | 107.1 | true | true | 1915 | 9.1408
Pipe-48901 | Junction-38294 | Junction-49190 | 97.66 | 0.225 | 107.1 | true | true | 1915 | 9.1408
Pipe-48940 | Junction-51620 | Junction-54123 | 10.82 | 0.166 | 43.1 | true | true | 172 | 0.821
Pipe-48941 | Junction-51622 | Junction-51620 | 1.4 | 0.18 | 54.5 | true | true | 321 | 1.5322
Pipe-48943 | Junction-51625 | Junction-51622 | 30.98 | 0.18 | 54.5 | true | true | 321 | 1.5322
Pipe-49038 | Junction-51737 | Junction-51524 | 45.17 | 0.225 | 107.1 | true | true | 1915 | 9.1408
Pipe-49408 | Junction-50272 | Junction-52634 | 79.23 | 0.217 | 82.5 | true | true | 962 | 4.5919
Pipe-49489 | Junction-51044 | Junction-50025 | 11.22 | 0.225 | 107.1 | true | true | 1915 | 9.1408
Pipe-49490 | Junction-52254 | Junction-52250 | 20.91 | 0.134 | 28.5 | true | true | 60 | 0.2864
Pipe-50093 | Junction-37788 | Junction-47852 | 20.01 | 0.225 | 107.1 | true | true | 1915 | 9.1408
Pipe-50123 | Junction-54909 | Junction-52880 | 26.69 | 0.134 | 28.5 | true | true | 60 | 0.2864
Pipe-50136 | Junction-52889 | Junction-37596 | 120.36 | 0.254 | 132.5 | true | true | 3354 | 16.0095
Pipe-50142 | Junction-48555 | Junction-52889 | 144.17 | 0.254 | 132.5 | true | true | 3354 | 16.0095
Pipe-50647 | Junction-53505 | Junction-51625 | 15.58 | 0.18 | 54.5 | true | true | 321 | 1.5322
Pipe-50686 | Junction-40767 | Junction-53612 | 538.3 | 0.254 | 132.5 | true | true | 3354 | 16.0095
Pipe-50712 | Junction-54877 | Junction-55179 | 19.35 | 0.134 | 28.5 | true | true | 60 | 0.2864
Pipe-50743 | Junction-53505 | Junction-57893 | 12.08 | 0.254 | 132.5 | true | true | 3354 | 16.0095
Pipe-50943 | Junction-53865 | Junction-53866 | 0.38 | 0.18 | 54.5 | true | true | 321 | 1.5322
Pipe-50944 | Junction-53865 | Junction-53867 | 0.36 | 0.18 | 54.5 | true | true | 321 | 1.5322
Pipe-50945 | Junction-897 | Junction-53865 | 98.99 | 0.205 | 70.3 | true | true | 630 | 3.0072
Pipe-51122 | Junction-54075 | Junction-54599 | 58.05 | 0.18 | 54.5 | true | true | 321 | 1.5322
Pipe-51164 | Junction-54115 | Junction-54809 | 73.78 | 0.134 | 28.5 | true | true | 60 | 0.2864
Pipe-51167 | Junction-54118 | Junction-54115 | 44.08 | 0.166 | 43.1 | true | true | 172 | 0.821
Pipe-51170 | Junction-51625 | Junction-54119 | 4.02 | 0.166 | 43.1 | true | true | 172 | 0.821
Pipe-51172 | Junction-51622 | Junction-54121 | 13.3 | 0.166 | 43.1 | true | true | 172 | 0.821
Pipe-51398 | Junction-47936 | Junction-51548 | 13.67 | 0.134 | 28.5 | true | true | 60 | 0.2864
Pipe-51504 | Junction-47934 | Junction-54387 | 24.72 | 0.134 | 28.5 | true | true | 60 | 0.2864
Pipe-51524 | Junction-37544 | Junction-55177 | 51.39 | 0.134 | 28.5 | true | true | 60 | 0.2864
Pipe-51546 | Junction-46131 | Junction-19916 | 360.62 | 0.411 | 312.7 | true | true | 31872 | 152.1337
Pipe-51587 | Junction-29936 | Junction-101660 | 419.38 | 0.282 | 160.3 | true | true | 5533 | 26.4105
Pipe-51626 | Junction-53612 | Junction-54634 | 21.91 | 0.134 | 28.5 | true | true | 60 | 0.2864
Pipe-51627 | Junction-43566 | Junction-52254 | 3 | 0.18 | 54.5 | true | true | 321 | 1.5322
Pipe-51633 | Junction-49026 | Junction-46121 | 10.59 | 0.18 | 54.5 | true | true | 321 | 1.5322
Pipe-51863 | Junction-49268 | Junction-54882 | 44.09 | 0.134 | 28.5 | true | true | 60 | 0.2864
Pipe-51927 | Junction-51072 | Junction-54948 | 36.07 | 0.18 | 54.5 | true | true | 321 | 1.5322
Pipe-52098 | Junction-13700 | Junction-66224 | 90.14 | 0.411 | 312.7 | true | true | 31872 | 152.1337
Pipe-52132 | Junction-54909 | Junction-55173 | 6.67 | 0.134 | 28.5 | true | true | 60 | 0.2864
Pipe-52133 | Junction-64134 | Junction-36301 | 64.5 | 0.225 | 107.1 | true | true | 1915 | 9.1408
Pipe-52289 | Junction-55365 | Junction-54877 | 49.79 | 0.18 | 54.5 | true | true | 321 | 1.5322
Pipe-52296 | Junction-51026 | Junction-48555 | 77.82 | 0.254 | 132.5 | true | true | 3354 | 16.0095
Pipe-52443 | Junction-55565 | Junction-55566 | 6.37 | 0.282 | 160.3 | true | true | 5533 | 26.4105
Pipe-52673 | Junction-55861 | Junction-53615 | 637.5 | 0.254 | 132.5 | true | true | 3354 | 16.0095
Pipe-52796 | Junction-56012 | Junction-38356 | 42.07 | 0.205 | 70.3 | true | true | 630 | 3.0072
Pipe-52891 | Junction-56146 | Junction-56147 | 2.79 | 0.166 | 43.1 | true | true | 172 | 0.821
Pipe-52981 | Junction-10519 | Junction-55861 | 47.88 | 0.254 | 132.5 | true | true | 3354 | 16.0095
Pipe-53098 | Junction-51737 | Junction-99304 | 106.62 | 0.205 | 70.3 | true | true | 630 | 3.0072
Pipe-53243 | Junction-49754 | Junction-50392 | 24.33 | 0.134 | 28.5 | true | true | 60 | 0.2864
Pipe-53247 | Junction-49754 | Junction-46214 | 7.4 | 0.18 | 54.5 | true | true | 321 | 1.5322
Pipe-53253 | Junction-52634 | Junction-38586 | 64.2 | 0.18 | 54.5 | true | true | 321 | 1.5322
Pipe-53395 | Junction-56780 | Junction-56779 | 8.53 | 0.134 | 28.5 | true | true | 60 | 0.2864
Pipe-53512 | Junction-14261 | Junction-7795 | 3476.59 | 0.404 | 393.8 | true | true | 58221 | 277.9045
Pipe-53632 | Junction-57062 | Junction-38425 | 69.37 | 0.205 | 70.3 | true | true | 630 | 3.0072
Pipe-53727 | Junction-74258 | Junction-57062 | 251.32 | 0.217 | 82.5 | true | true | 962 | 4.5919
Pipe-53828 | Junction-50404 | Junction-50470 | 44.18 | 0.18 | 54.5 | true | true | 321 | 1.5322
Pipe-53833 | Junction-48934 | Junction-57301 | 67.1 | 0.18 | 54.5 | true | true | 321 | 1.5322
Pipe-53995 | Junction-52634 | Junction-54599 | 10.6 | 0.205 | 70.3 | true | true | 630 | 3.0072
Pipe-54287 | Junction-57893 | Junction-41082 | 72.63 | 0.254 | 132.5 | true | true | 3354 | 16.0095
Pipe-54407 | Junction-47051 | Junction-60463 | 57.57 | 0.166 | 43.1 | true | true | 172 | 0.821
Pipe-54764 | Junction-56012 | Junction-58481 | 26.12 | 0.134 | 28.5 | true | true | 60 | 0.2864
Pipe-54905 | Junction-58780 | Junction-58647 | 44.69 | 0.134 | 28.5 | true | true | 60 | 0.2864
Pipe-55000 | Junction-56361 | Junction-58769 | 18.9 | 0.134 | 28.5 | true | true | 60 | 0.2864
Pipe-55018 | Junction-58790 | Junction-58784 | 22.77 | 0.134 | 28.5 | true | true | 60 | 0.2864
Pipe-55374 | Junction-59203 | Junction-7795 | 471.34 | 0.404 | 393.8 | true | true | 58221 | 277.9045
Pipe-55709 | Junction-59693 | Junction-56361 | 34.61 | 0.254 | 132.5 | true | true | 3354 | 16.0095
Pipe-55865 | Junction-56780 | Junction-45888 | 5.39 | 0.18 | 54.5 | true | true | 321 | 1.5322
Pipe-56287 | Junction-50281 | Junction-51815 | 23.18 | 0.134 | 28.5 | true | true | 60 | 0.2864
Pipe-56365 | Junction-60463 | Junction-54909 | 2.18 | 0.134 | 28.5 | true | true | 60 | 0.2864
Pipe-56412 | Junction-50404 | Junction-53505 | 139.07 | 0.254 | 132.5 | true | true | 3354 | 16.0095
Pipe-56415 | Junction-60532 | Junction-60533 | 6.52 | 0.18 | 54.5 | true | true | 321 | 1.5322
Pipe-56489 | Junction-60613 | Junction-34547 | 46.13 | 0.225 | 107.1 | true | true | 1915 | 9.1408
Pipe-56521 | Junction-6737 | Junction-128917 | 169.61 | 0.404 | 393.8 | true | true | 58221 | 277.9045
Pipe-56687 | Junction-54179 | Junction-40767 | 100.14 | 0.254 | 132.5 | true | true | 3354 | 16.0095
Pipe-56933 | Junction-61715 | Junction-60758 | 50.35 | 0.134 | 28.5 | true | true | 60 | 0.2864
Pipe-57106 | Junction-14297 | Junction-7222 | 1245.74 | 0.411 | 312.7 | true | true | 31872 | 152.1337
Pipe-57350 | Junction-36962 | Junction-61767 | 1.18 | 0.18 | 54.5 | true | true | 321 | 1.5322
Pipe-57352 | Junction-65373 | Junction-61769 | 34.51 | 0.134 | 28.5 | true | true | 60 | 0.2864
Pipe-58425 | Junction-2040 | Kirkkonummi | 3.68 | 0.355 | 263 | true | true | 20264 | 96.7255
Pipe-58648 | Junction-14292 | Junction-14297 | 101.52 | 0.411 | 312.7 | true | true | 31872 | 152.1337
Pipe-58759 | Junction-63624 | Junction-38195 | 25.94 | 0.166 | 43.1 | true | true | 172 | 0.821
Pipe-58862 | Junction-38805 | Junction-63624 | 5.2 | 0.166 | 43.1 | true | true | 172 | 0.821
Pipe-58863 | Junction-36958 | Junction-36960 | 8.59 | 0.134 | 28.5 | true | true | 60 | 0.2864
Pipe-58865 | Junction-61767 | Junction-63760 | 23.27 | 0.134 | 28.5 | true | true | 60 | 0.2864
Pipe-58870 | Junction-36951 | Junction-37780 | 26.48 | 0.134 | 28.5 | true | true | 60 | 0.2864
Pipe-58876 | Junction-65234 | Junction-63769 | 41.18 | 0.134 | 28.5 | true | true | 60 | 0.2864
Pipe-58887 | Junction-14279 | Junction-59203 | 108.03 | 0.411 | 312.7 | true | true | 31872 | 152.1337
Pipe-59076 | Junction-64013 | Junction-39152 | 57.14 | 0.205 | 70.3 | true | true | 630 | 3.0072
Pipe-59078 | Junction-64013 | Junction-99479 | 53.41 | 0.254 | 132.5 | true | true | 3354 | 16.0095
Pipe-59271 | Junction-64662 | Junction-64230 | 18.76 | 0.166 | 43.1 | true | true | 172 | 0.821
Pipe-59333 | Junction-38652 | Junction-39122 | 72.52 | 0.205 | 70.3 | true | true | 630 | 3.0072
Pipe-59665 | Junction-64665 | Junction-64664 | 29.77 | 0.134 | 28.5 | true | true | 60 | 0.2864
Pipe-59742 | Junction-64781 | Junction-64780 | 10.65 | 0.134 | 28.5 | true | true | 60 | 0.2864
Pipe-60117 | Junction-39059 | Junction-65236 | 9.83 | 0.134 | 28.5 | true | true | 60 | 0.2864
Pipe-60184 | Junction-65818 | Junction-67935 | 30.59 | 0.166 | 43.1 | true | true | 172 | 0.821
Pipe-60222 | Junction-39069 | Junction-65376 | 19.42 | 0.134 | 28.5 | true | true | 60 | 0.2864
Pipe-60457 | Junction-38460 | Junction-65680 | 26.66 | 0.134 | 28.5 | true | true | 60 | 0.2864
Pipe-60478 | Junction-57893 | Junction-65709 | 37.52 | 0.166 | 43.1 | true | true | 172 | 0.821
Pipe-60503 | Junction-37764 | Junction-65240 | 48.46 | 0.134 | 28.5 | true | true | 60 | 0.2864
Pipe-60559 | Junction-38195 | Junction-38706 | 53.22 | 0.134 | 28.5 | true | true | 60 | 0.2864
Pipe-60922 | Junction-68937 | Junction-66227 | 26.45 | 0.134 | 28.5 | true | true | 60 | 0.2864
Pipe-61161 | Junction-39409 | Junction-66516 | 21.04 | 0.134 | 28.5 | true | true | 60 | 0.2864
Pipe-61437 | Junction-58780 | Junction-56012 | 32.58 | 0.205 | 70.3 | true | true | 630 | 3.0072
Pipe-61614 | Junction-39069 | Junction-39059 | 51.42 | 0.217 | 82.5 | true | true | 962 | 4.5919
Pipe-61853 | Junction-60532 | Junction-67029 | 22.54 | 0.134 | 28.5 | true | true | 60 | 0.2864
Pipe-61909 | Junction-99783 | Junction-56146 | 87.42 | 0.225 | 107.1 | true | true | 1915 | 9.1408
Pipe-62086 | Junction-66224 | Junction-13715 | 288.9 | 0.411 | 312.7 | true | true | 31872 | 152.1337
Pipe-62354 | Junction-66224 | Junction-68937 | 70.36 | 0.18 | 54.5 | true | true | 321 | 1.5322
Pipe-62424 | Junction-67965 | Junction-67964 | 5.23 | 0.134 | 28.5 | true | true | 60 | 0.2864
Pipe-62425 | Junction-67965 | Junction-67966 | 2.49 | 0.134 | 28.5 | true | true | 60 | 0.2864
Pipe-62448 | Junction-36962 | Junction-65422 | 29.95 | 0.134 | 28.5 | true | true | 60 | 0.2864
Pipe-62697 | Junction-37550 | Junction-58790 | 14.43 | 0.18 | 54.5 | true | true | 321 | 1.5322
Pipe-62713 | Junction-38492 | Junction-67965 | 37.56 | 0.166 | 43.1 | true | true | 172 | 0.821
Pipe-63116 | Junction-38356 | Junction-68672 | 47.38 | 0.134 | 28.5 | true | true | 60 | 0.2864
Pipe-63203 | Junction-36967 | Neidonkallio_EMP_1 | 22.07 | 0.134 | 28.5 | true | true | 60 | 0.2864
Pipe-63384 | Junction-68937 | Junction-68938 | 6 | 0.18 | 54.5 | true | true | 321 | 1.5322
Pipe-63553 | Junction-36967 | Junction-48315 | 8.18 | 0.18 | 54.5 | true | true | 321 | 1.5322
Pipe-63557 | Junction-65373 | Junction-36962 | 33.94 | 0.18 | 54.5 | true | true | 321 | 1.5322
Pipe-63657 | Junction-61715 | Junction-65373 | 21.92 | 0.18 | 54.5 | true | true | 321 | 1.5322
Pipe-63658 | Junction-36958 | Junction-61715 | 1.01 | 0.18 | 54.5 | true | true | 321 | 1.5322
Pipe-63815 | Junction-38803 | Junction-38805 | 90.6 | 0.205 | 70.3 | true | true | 630 | 3.0072
Pipe-64037 | Junction-69578 | Junction-100121 | 93.16 | 0.217 | 82.5 | true | true | 962 | 4.5919
Pipe-64038 | Junction-69578 | Junction-73674 | 43.39 | 0.166 | 43.1 | true | true | 172 | 0.821
Pipe-64111 | Junction-73054 | Junction-72632 | 140.93 | 0.18 | 54.5 | true | true | 321 | 1.5322
Pipe-64488 | Junction-37544 | Junction-37550 | 50.96 | 0.205 | 70.3 | true | true | 630 | 3.0072
Pipe-64538 | Junction-55365 | Junction-65818 | 80.46 | 0.217 | 82.5 | true | true | 962 | 4.5919
Pipe-64712 | Junction-36968 | Junction-39409 | 58.84 | 0.18 | 54.5 | true | true | 321 | 1.5322
Pipe-64737 | Junction-38463 | Junction-56780 | 18.7 | 0.18 | 54.5 | true | true | 321 | 1.5322
Pipe-64833 | Junction-58790 | Junction-38463 | 25.86 | 0.18 | 54.5 | true | true | 321 | 1.5322
Pipe-65130 | Junction-37764 | Junction-38492 | 58.26 | 0.217 | 82.5 | true | true | 962 | 4.5919
Pipe-65171 | Junction-48140 | Junction-65234 | 120.58 | 0.225 | 107.1 | true | true | 1915 | 9.1408
Pipe-65223 | Junction-37550 | Junction-36951 | 70.8 | 0.18 | 54.5 | true | true | 321 | 1.5322
Pipe-66069 | Junction-71707 | Junction-71599 | 25.51 | 0.166 | 43.1 | true | true | 172 | 0.821
Pipe-66129 | Junction-71707 | Junction-76728 | 64.76 | 0.205 | 70.3 | true | true | 630 | 3.0072
Pipe-66220 | Junction-13715 | Junction-40889 | 666.38 | 0.411 | 312.7 | true | true | 31872 | 152.1337
Pipe-66589 | Junction-64275 | Junction-70718 | 2.48 | 0.225 | 107.1 | true | true | 1915 | 9.1408
Pipe-66590 | Junction-65234 | Junction-64275 | 27.71 | 0.225 | 107.1 | true | true | 1915 | 9.1408
Pipe-66833 | Junction-37396 | Junction-64662 | 6.23 | 0.225 | 107.1 | true | true | 1915 | 9.1408
Pipe-67123 | Junction-72630 | Junction-55365 | 18.03 | 0.217 | 82.5 | true | true | 962 | 4.5919
Pipe-67461 | Junction-47090 | Junction-7222 | 106.69 | 0.411 | 312.7 | true | true | 31872 | 152.1337
Pipe-67466 | Junction-40889 | Junction-47090 | 164.09 | 0.411 | 312.7 | true | true | 31872 | 152.1337
Pipe-67844 | Junction-73296 | Junction-73295 | 19.36 | 1 | 100 | true | true | 1915 | 9.1408
Pipe-67845 | Junction-73296 | Junction-73297 | 2.85 | 1 | 100 | true | true | 1915 | 9.1408
Pipe-68855 | Junction-74257 | Junction-74258 | 78.69 | 0.217 | 82.5 | true | true | 962 | 4.5919
Pipe-69054 | Junction-65818 | Junction-74257 | 198.34 | 0.217 | 82.5 | true | true | 962 | 4.5919
Pipe-69099 | Junction-74498 | Junction-100018 | 34.43 | 0.217 | 82.5 | true | true | 962 | 4.5919
Pipe-70120 | Junction-75386 | Junction-71707 | 37.98 | 0.205 | 70.3 | true | true | 630 | 3.0072
Pipe-70121 | Junction-75386 | Junction-75387 | 2.73 | 0.217 | 82.5 | true | true | 962 | 4.5919
Pipe-70122 | Junction-75388 | Junction-75389 | 1.71 | 0.166 | 43.1 | true | true | 172 | 0.821
Pipe-70265 | Junction-74257 | Junction-75222 | 44.84 | 0.166 | 43.1 | true | true | 172 | 0.821
Pipe-70411 | Junction-75752 | Junction-75388 | 38.74 | 0.18 | 54.5 | true | true | 321 | 1.5322
Pipe-70521 | Junction-75752 | Junction-75753 | 17.85 | 0.18 | 54.5 | true | true | 321 | 1.5322
Pipe-71179 | Junction-77288 | Junction-73056 | 67.99 | 0.18 | 54.5 | true | true | 321 | 1.5322
Pipe-71700 | Junction-76728 | Junction-72077 | 22.5 | 0.166 | 43.1 | true | true | 172 | 0.821
Pipe-71739 | Junction-74258 | Hommaksenkaari_EMP | 35.6 | 0.166 | 43.1 | true | true | 172 | 0.821
Pipe-71772 | Junction-37845 | Junction-76786 | 105.94 | 0.18 | 54.5 | true | true | 321 | 1.5322
Pipe-72048 | Junction-75388 | Junction-76989 | 1.79 | 0.166 | 43.1 | true | true | 172 | 0.821
Pipe-72412 | Junction-73054 | Junction-77288 | 1.7 | 0.217 | 82.5 | true | true | 962 | 4.5919
Pipe-73738 | Junction-55861 | Junction-74927 | 13.83 | 0.18 | 54.5 | true | true | 321 | 1.5322
Pipe-78220 | Junction-38652 | Junction-84540 | 2.63 | 0.134 | 28.5 | true | true | 60 | 0.2864
Pipe-92653 | Junction-50543 | Junction-41132 | 43.93 | 0.303 | 107.1 | true | true | 1915 | 9.1408
Pipe-93431 | Junction-9062 | Junction-105560 | 35.5 | 0.436 | 160.3 | true | true | 5533 | 26.4105
Pipe-94214 | Junction-94517 | Junction-94512 | 37.67 | 0.225 | 107.1 | true | true | 1915 | 9.1408
Pipe-94217 | Junction-94517 | Junction-95634 | 18.67 | 0.303 | 107.1 | true | true | 1915 | 9.1408
Pipe-94317 | Junction-96454 | Junction-94619 | 15.4 | 0.191 | 43.1 | true | true | 172 | 0.821
Pipe-94896 | Junction-95084 | Junction-84173 | 83.92 | 0.213 | 54.5 | true | true | 321 | 1.5322
Pipe-94898 | Junction-95085 | Junction-95084 | 6.53 | 0.248 | 70.3 | true | true | 630 | 3.0072
Pipe-95061 | Junction-95215 | Junction-95216 | 35.26 | 0.259 | 82.5 | true | true | 962 | 4.5919
Pipe-95141 | Junction-95284 | Junction-95285 | 28.23 | 0.303 | 107.1 | true | true | 1915 | 9.1408
Pipe-95142 | Junction-95284 | Junction-95286 | 11.67 | 0.191 | 43.1 | true | true | 172 | 0.821
Pipe-95193 | Junction-95240 | Junction-95242 | 69.06 | 0.191 | 43.1 | true | true | 172 | 0.821
Pipe-95212 | Junction-95216 | Junction-95240 | 9.11 | 0.259 | 82.5 | true | true | 962 | 4.5919
Pipe-95214 | Junction-95216 | Junction-95354 | 17.77 | 1 | 100 | true | true | 1915 | 9.1408
Pipe-95329 | Junction-21321 | Junction-47600 | 203.51 | 0.37 | 210.1 | true | true | 11253 | 53.7136
Pipe-95559 | Junction-64781 | Junction-95618 | 20.69 | 0.303 | 107.1 | true | true | 1915 | 9.1408
Pipe-95573 | Junction-95634 | Junction-95635 | 28.36 | 0.191 | 43.1 | true | true | 172 | 0.821
Pipe-95806 | Junction-94512 | Junction-93415 | 41.38 | 0.191 | 43.1 | true | true | 172 | 0.821
Pipe-95932 | Junction-96514 | Junction-96454 | 141.78 | 0.364 | 132.5 | true | true | 3354 | 16.0095
Pipe-96040 | Junction-95618 | Junction-95940 | 1.81 | 0.217 | 82.5 | true | true | 962 | 4.5919
Pipe-96046 | Junction-95618 | Junction-95942 | 100.93 | 0.191 | 43.1 | true | true | 172 | 0.821
Pipe-96386 | Junction-96222 | Junction-26246 | 24.17 | 0.191 | 43.1 | true | true | 172 | 0.821
Pipe-96387 | Junction-96224 | Junction-96222 | 28.77 | 0.37 | 210.1 | true | true | 11253 | 53.7136
Pipe-96388 | Junction-96224 | Junction-96226 | 120.06 | 0.205 | 70.3 | true | true | 630 | 3.0072
Pipe-96725 | Junction-18021 | Junction-2007 | 121.25 | 0.306 | 132.5 | true | true | 3354 | 16.0095
Pipe-96825 | Junction-95940 | Junction-71596 | 44.07 | 0.217 | 82.5 | true | true | 962 | 4.5919
Pipe-96853 | Junction-94950 | Junction-102277 | 321.52 | 0.303 | 107.1 | true | true | 1915 | 9.1408
Pipe-96860 | Junction-96634 | Junction-96635 | 6.98 | 0.252 | 43.1 | true | true | 172 | 0.821
Pipe-97121 | Junction-96845 | Junction-96846 | 3.41 | 0.191 | 43.1 | true | true | 172 | 0.821
Pipe-97122 | Junction-96849 | Junction-96845 | 9.16 | 0.248 | 70.3 | true | true | 630 | 3.0072
Pipe-97125 | Junction-96849 | Junction-96850 | 10.44 | 0.191 | 43.1 | true | true | 172 | 0.821
Pipe-97126 | Junction-95285 | Junction-96849 | 4.81 | 0.248 | 70.3 | true | true | 630 | 3.0072
Pipe-97176 | Junction-96958 | Junction-95284 | 105.8 | 0.303 | 107.1 | true | true | 1915 | 9.1408
Pipe-97240 | Junction-95240 | Junction-96634 | 62.52 | 0.259 | 82.5 | true | true | 962 | 4.5919
Pipe-97278 | Junction-96962 | Junction-96963 | 8.55 | 0.243 | 54.5 | true | true | 321 | 1.5322
Pipe-97456 | Junction-96512 | Junction-96810 | 273.72 | 0.303 | 107.1 | true | true | 1915 | 9.1408
Pipe-97486 | Junction-32341 | Junction-97113 | 296.24 | 0.303 | 107.1 | true | true | 1915 | 9.1408
Pipe-97488 | Junction-31656 | Junction-32340 | 37.81 | 0.303 | 107.1 | true | true | 1915 | 9.1408
Pipe-97491 | Junction-9137 | Junction-9115 | 38.82 | 0.483 | 210.1 | true | true | 11253 | 53.7136
Pipe-97732 | Junction-94616 | Junction-96577 | 11.03 | 0.364 | 132.5 | true | true | 3354 | 16.0095
Pipe-97733 | Junction-94616 | Junction-97299 | 11.14 | 1 | 100 | true | true | 1915 | 9.1408
Pipe-97823 | Junction-31657 | Junction-42312 | 36.64 | 0.18 | 54.5 | true | true | 321 | 1.5322
Pipe-98015 | Junction-94616 | Junction-96454 | 110.14 | 0.364 | 132.5 | true | true | 3354 | 16.0095
Pipe-98037 | Junction-96514 | Junction-97499 | 12.51 | 0.191 | 43.1 | true | true | 172 | 0.821
Pipe-98046 | Junction-96810 | Junction-97501 | 287.96 | 0.259 | 82.5 | true | true | 962 | 4.5919
Pipe-98089 | Junction-96577 | Junction-97159 | 29.28 | 0.303 | 107.1 | true | true | 1915 | 9.1408
Pipe-98152 | Junction-97575 | Junction-97576 | 90.55 | 0.213 | 54.5 | true | true | 321 | 1.5322
Pipe-98155 | Junction-96577 | Junction-97575 | 173.33 | 0.364 | 132.5 | true | true | 3354 | 16.0095
Pipe-98390 | Junction-97749 | Junction-3165 | 30.85 | 0.364 | 132.5 | true | true | 3354 | 16.0095
Pipe-98394 | Junction-97751 | Junction-97749 | 65.37 | 0.303 | 107.1 | true | true | 1915 | 9.1408
Pipe-98395 | Junction-97753 | Junction-97754 | 40.08 | 0.248 | 70.3 | true | true | 630 | 3.0072
Pipe-98398 | Junction-97373 | Junction-120722 | 30.36 | 0.259 | 82.5 | true | true | 962 | 4.5919
Pipe-98403 | Junction-97767 | Junction-99902 | 43.61 | 0.134 | 28.5 | true | true | 60 | 0.2864
Pipe-98408 | Junction-97767 | Junction-97769 | 9.68 | 0.166 | 43.1 | true | true | 172 | 0.821
Pipe-98410 | Junction-50282 | Junction-97767 | 18.22 | 0.166 | 43.1 | true | true | 172 | 0.821
Pipe-98412 | Junction-99010 | Junction-99830 | 176.72 | 0.254 | 132.5 | true | true | 3354 | 16.0095
Pipe-98414 | Junction-97775 | Junction-97774 | 19.9 | 1 | 100 | true | true | 1915 | 9.1408
Pipe-98415 | Junction-97775 | Junction-40791 | 26.03 | 1 | 100 | true | true | 1915 | 9.1408
Pipe-98645 | Junction-97937 | Junction-9252 | 26.9 | 0.37 | 210.1 | true | true | 11253 | 53.7136
Pipe-98721 | Junction-95084 | Junction-97993 | 51.48 | 0.248 | 70.3 | true | true | 630 | 3.0072
Pipe-98728 | Junction-95085 | Junction-40961 | 5.32 | 0.248 | 70.3 | true | true | 630 | 3.0072
Pipe-98998 | Junction-95940 | Junction-31657 | 104.7 | 0.18 | 54.5 | true | true | 321 | 1.5322
Pipe-99033 | Junction-4364 | Junction-1704 | 89.07 | 0.436 | 160.3 | true | true | 5533 | 26.4105
Pipe-99037 | Junction-98224 | Junction-4364 | 36.31 | 0.436 | 160.3 | true | true | 5533 | 26.4105
Pipe-99055 | Junction-98243 | Junction-909 | 34.09 | 0.364 | 132.5 | true | true | 3354 | 16.0095
Pipe-99076 | Junction-96963 | Junction-98261 | 7.69 | 0.252 | 43.1 | true | true | 172 | 0.821
Pipe-99077 | Junction-96963 | Junction-98262 | 4.65 | 0.252 | 43.1 | true | true | 172 | 0.821
Pipe-99111 | Junction-96845 | Junction-95085 | 63.13 | 0.248 | 70.3 | true | true | 630 | 3.0072
Pipe-99266 | Junction-96958 | Junction-98390 | 31.95 | 0.191 | 43.1 | true | true | 172 | 0.821
Pipe-99279 | Junction-98397 | Junction-96514 | 3.87 | 0.364 | 132.5 | true | true | 3354 | 16.0095
Pipe-99283 | Junction-96512 | Junction-98399 | 53.57 | 0.191 | 43.1 | true | true | 172 | 0.821
Pipe-99286 | Junction-98397 | Junction-96512 | 8.75 | 1 | 100 | true | true | 1915 | 9.1408
Pipe-99290 | Junction-3673 | Junction-4076 | 114.24 | 0.364 | 132.5 | true | true | 3354 | 16.0095
Pipe-99300 | Junction-42761 | Junction-98413 | 13.85 | 0.166 | 43.1 | true | true | 172 | 0.821
Pipe-99304 | Junction-9041 | Junction-31656 | 56.54 | 0.303 | 107.1 | true | true | 1915 | 9.1408
Pipe-99520 | Junction-920 | Junction-917 | 0.81 | 0.483 | 210.1 | true | true | 11253 | 53.7136
Pipe-99521 | Junction-34066 | Junction-98582 | 36.43 | 0.191 | 43.1 | true | true | 172 | 0.821
Pipe-99531 | Junction-97373 | Junction-97751 | 120.99 | 0.364 | 132.5 | true | true | 3354 | 16.0095
Pipe-99645 | Junction-98673 | Junction-98583 | 23.88 | 0.213 | 54.5 | true | true | 321 | 1.5322
Pipe-99648 | Junction-34066 | Junction-98673 | 26.29 | 0.259 | 82.5 | true | true | 962 | 4.5919
Pipe-99651 | Junction-920 | Junction-33846 | 43.21 | 0.259 | 82.5 | true | true | 962 | 4.5919
Pipe-99654 | Junction-98243 | Junction-98676 | 8.7 | 0.191 | 43.1 | true | true | 172 | 0.821
Pipe-99687 | Junction-96962 | Junction-66675 | 192.25 | 0.259 | 82.5 | true | true | 962 | 4.5919
Pipe-99695 | Junction-98710 | Junction-99326 | 86.95 | 0.293 | 210.1 | true | true | 11253 | 53.7136
Pipe-99712 | Junction-98717 | Junction-98718 | 17.75 | 1 | 100 | true | true | 1915 | 9.1408
Pipe-99713 | Junction-98719 | Junction-98717 | 5.34 | 1 | 100 | true | true | 1915 | 9.1408
Pipe-99714 | Junction-98720 | Junction-98719 | 11.35 | 0.217 | 82.5 | true | true | 962 | 4.5919
Pipe-99715 | Junction-98720 | Junction-98721 | 4.85 | 1 | 100 | true | true | 1915 | 9.1408
Pipe-99716 | Junction-98722 | Junction-98723 | 15.6 | 1 | 100 | true | true | 1915 | 9.1408
Pipe-99717 | Junction-98724 | Junction-98725 | 14.56 | 1 | 100 | true | true | 1915 | 9.1408
Pipe-99815 | Junction-98224 | Junction-30008 | 46.28 | 0.259 | 82.5 | true | true | 962 | 4.5919
Pipe-99847 | Junction-98841 | Junction-98833 | 72 | 0.18 | 54.5 | true | true | 321 | 1.5322
Pipe-99854 | Junction-98841 | Junction-99485 | 89.41 | 0.254 | 132.5 | true | true | 3354 | 16.0095
Pipe-99856 | Junction-98849 | Junction-98844 | 90.72 | 0.166 | 43.1 | true | true | 172 | 0.821
Pipe-99865 | Junction-99130 | Junction-98849 | 69.28 | 0.205 | 70.3 | true | true | 630 | 3.0072
Pipe-99870 | Junction-98860 | Junction-98858 | 21.35 | 1 | 100 | true | true | 1915 | 9.1408
Pipe-99878 | Junction-98869 | Junction-98870 | 11.76 | 1 | 100 | true | true | 1915 | 9.1408
Pipe-99880 | Junction-98873 | Junction-98869 | 124.08 | 0.282 | 160.3 | true | true | 5533 | 26.4105
Pipe-99882 | Junction-98874 | Junction-98875 | 7.74 | 1 | 100 | true | true | 1915 | 9.1408
Pipe-99883 | Junction-98874 | Junction-98876 | 7.42 | 1 | 100 | true | true | 1915 | 9.1408
Pipe-99884 | Junction-98873 | Junction-98874 | 33.81 | 1 | 100 | true | true | 1915 | 9.1408
Pipe-99885 | Junction-98882 | Junction-98873 | 46.14 | 0.282 | 160.3 | true | true | 5533 | 26.4105
Pipe-99886 | Junction-98878 | Junction-98879 | 7.22 | 1 | 100 | true | true | 1915 | 9.1408
Pipe-99888 | Junction-98882 | Junction-98881 | 35.46 | 1 | 100 | true | true | 1915 | 9.1408
Pipe-99890 | Junction-98878 | Junction-98882 | 1.41 | 0.282 | 160.3 | true | true | 5533 | 26.4105
Pipe-99916 | Junction-98867 | Junction-99110 | 97.49 | 0.37 | 210.1 | true | true | 11253 | 53.7136
Pipe-99917 | Junction-98907 | Junction-98908 | 6.87 | 1 | 100 | true | true | 1915 | 9.1408
Pipe-99918 | Junction-98909 | Junction-98910 | 17.2 | 1 | 100 | true | true | 1915 | 9.1408
Pipe-99920 | Junction-98907 | Junction-98912 | 38.28 | 1 | 100 | true | true | 1915 | 9.1408
Pipe-99923 | Junction-98909 | Junction-98907 | 10.31 | 1 | 100 | true | true | 1915 | 9.1408
Pipe-99924 | Junction-98867 | Junction-98909 | 24.27 | 1 | 100 | true | true | 1915 | 9.1408
Pipe-99934 | Junction-98926 | Junction-98927 | 3.7 | 1 | 100 | true | true | 1915 | 9.1408
Pipe-99943 | Junction-98936 | Junction-39156 | 28.42 | 0.254 | 132.5 | true | true | 3354 | 16.0095
Pipe-99977 | Junction-99368 | Junction-16278 | 440.55 | 0.217 | 82.5 | true | true | 962 | 4.5919
Pipe-100021 | Junction-99010 | Junction-8112 | 60.09 | 0.217 | 82.5 | true | true | 962 | 4.5919
Pipe-100029 | Junction-98860 | Junction-65528 | 44.35 | 0.254 | 132.5 | true | true | 3354 | 16.0095
Pipe-100033 | Junction-99018 | Junction-99019 | 9.71 | 0.293 | 210.1 | true | true | 11253 | 53.7136
Pipe-100034 | Junction-99321 | Junction-99182 | 322.52 | 0.225 | 107.1 | true | true | 1915 | 9.1408
Pipe-100050 | Junction-59693 | Junction-54179 | 614.95 | 0.411 | 312.7 | true | true | 31872 | 152.1337
Pipe-100059 | Junction-99052 | Junction-99051 | 18.29 | 1 | 100 | true | true | 1915 | 9.1408
Pipe-100061 | Junction-60613 | Junction-99052 | 76.22 | 0.282 | 160.3 | true | true | 5533 | 26.4105
Pipe-100062 | Junction-99053 | Junction-99054 | 10.78 | 0.259 | 82.5 | true | true | 962 | 4.5919
Pipe-100063 | Junction-2360 | Junction-99053 | 91.73 | 0.259 | 82.5 | true | true | 962 | 4.5919
Pipe-100086 | Junction-99073 | Junction-99074 | 6.1 | 1 | 100 | true | true | 1915 | 9.1408
Pipe-100087 | Junction-99075 | Junction-99076 | 8.08 | 1 | 100 | true | true | 1915 | 9.1408
Pipe-100088 | Junction-99075 | Junction-99077 | 11.97 | 1 | 100 | true | true | 1915 | 9.1408
Pipe-100089 | Junction-99080 | Junction-99079 | 21.25 | 1 | 100 | true | true | 1915 | 9.1408
Pipe-100091 | Junction-99080 | Junction-64021 | 25.33 | 0.217 | 82.5 | true | true | 962 | 4.5919
Pipe-100092 | Junction-99006 | Junction-99081 | 20.46 | 1 | 100 | true | true | 1915 | 9.1408
Pipe-100093 | Junction-99006 | Junction-99080 | 19 | 0.217 | 82.5 | true | true | 962 | 4.5919
Pipe-100094 | Junction-8112 | Junction-99082 | 7.68 | 1 | 100 | true | true | 1915 | 9.1408
Pipe-100095 | Junction-8112 | Junction-99006 | 28.63 | 0.217 | 82.5 | true | true | 962 | 4.5919
Pipe-100096 | Junction-99083 | Junction-99084 | 22.17 | 0.134 | 28.5 | true | true | 60 | 0.2864
Pipe-100097 | Junction-99083 | Junction-99085 | 14.09 | 1 | 100 | true | true | 1915 | 9.1408
Pipe-100098 | Junction-99088 | Junction-99087 | 19.64 | 1 | 100 | true | true | 1915 | 9.1408
Pipe-100100 | Junction-99089 | Junction-99090 | 12.86 | 1 | 100 | true | true | 1915 | 9.1408
Pipe-100101 | Junction-99089 | Junction-99088 | 13.93 | 0.217 | 82.5 | true | true | 962 | 4.5919
Pipe-100103 | Junction-99462 | Junction-99093 | 22.96 | 1 | 100 | true | true | 1915 | 9.1408
Pipe-100104 | Junction-99094 | Junction-99095 | 5.69 | 1 | 100 | true | true | 1915 | 9.1408
Pipe-100105 | Junction-99094 | Junction-99096 | 4.62 | 1 | 100 | true | true | 1915 | 9.1408
Pipe-100123 | Junction-99114 | Junction-99115 | 16.11 | 0.282 | 160.3 | true | true | 5533 | 26.4105
Pipe-100124 | Junction-100381 | Junction-100225 | 119.31 | 0.282 | 160.3 | true | true | 5533 | 26.4105
Pipe-100125 | Junction-99121 | Junction-99119 | 6.56 | 0.166 | 43.1 | true | true | 172 | 0.821
Pipe-100135 | Junction-47088 | Junction-99130 | 21.56 | 0.37 | 210.1 | true | true | 11253 | 53.7136
Pipe-100138 | Junction-98867 | Junction-99133 | 118.38 | 0.37 | 210.1 | true | true | 11253 | 53.7136
Pipe-100211 | Junction-99182 | Junction-51737 | 2.39 | 0.205 | 70.3 | true | true | 630 | 3.0072
Pipe-100216 | Junction-99513 | Junction-99186 | 15.66 | 1 | 100 | true | true | 1915 | 9.1408
Pipe-100266 | Junction-99226 | Junction-99794 | 111.99 | 0.166 | 43.1 | true | true | 172 | 0.821
Pipe-100280 | Junction-99237 | Junction-99238 | 1.15 | 1 | 100 | true | true | 1915 | 9.1408
Pipe-100288 | Junction-65389 | Junction-99247 | 3.94 | 0.166 | 43.1 | true | true | 172 | 0.821
Pipe-100327 | Junction-15412 | Junction-18021 | 33.8 | 0.306 | 132.5 | true | true | 3354 | 16.0095
Pipe-100328 | Junction-99277 | Junction-99278 | 5.38 | 0.282 | 160.3 | true | true | 5533 | 26.4105
Pipe-100339 | Junction-22175 | Junction-99286 | 119.15 | 0.18 | 54.5 | true | true | 321 | 1.5322
Pipe-100346 | Junction-64134 | Junction-99292 | 99.34 | 1 | 100 | true | true | 1915 | 9.1408
Pipe-100347 | Junction-19194 | Junction-19191 | 17.72 | 0.282 | 160.3 | true | true | 5533 | 26.4105
Pipe-100358 | Junction-64021 | Junction-99075 | 2.25 | 1 | 100 | true | true | 1915 | 9.1408
Pipe-100365 | Junction-41031 | Junction-99307 | 73.55 | 0.166 | 43.1 | true | true | 172 | 0.821
Pipe-100378 | Junction-99321 | Junction-99319 | 55.17 | 0.217 | 82.5 | true | true | 962 | 4.5919
Pipe-100384 | Junction-99053 | Junction-99323 | 5.51 | 1 | 100 | true | true | 1915 | 9.1408
Pipe-100390 | Junction-99330 | Junction-99703 | 4.64 | 0.217 | 82.5 | true | true | 962 | 4.5919
Pipe-100416 | Junction-99350 | Junction-99351 | 43.06 | 0.213 | 54.5 | true | true | 321 | 1.5322
Pipe-100432 | Junction-99360 | Junction-99361 | 8.41 | 1 | 100 | true | true | 1915 | 9.1408
Pipe-100433 | Junction-99364 | Junction-99363 | 6.24 | 1 | 100 | true | true | 1915 | 9.1408
Pipe-100435 | Junction-99360 | Junction-99364 | 14.82 | 0.282 | 160.3 | true | true | 5533 | 26.4105
Pipe-100439 | Junction-30728 | Junction-99360 | 113.6 | 0.282 | 160.3 | true | true | 5533 | 26.4105
Pipe-100440 | Junction-99368 | Junction-30728 | 0.71 | 0.282 | 160.3 | true | true | 5533 | 26.4105
Pipe-100446 | Junction-99376 | Junction-99377 | 2.77 | 1 | 100 | true | true | 1915 | 9.1408
Pipe-100472 | Junction-99130 | Junction-99395 | 51.29 | 0.37 | 210.1 | true | true | 11253 | 53.7136
Pipe-100513 | Junction-99438 | Junction-99350 | 6.1 | 1 | 100 | true | true | 1915 | 9.1408
Pipe-100554 | Junction-99461 | Junction-99094 | 13.14 | 1 | 100 | true | true | 1915 | 9.1408
Pipe-100556 | Junction-99463 | Junction-99464 | 4.84 | 1 | 100 | true | true | 1915 | 9.1408
Pipe-100557 | Junction-99088 | Junction-99465 | 28.68 | 1 | 100 | true | true | 1915 | 9.1408
Pipe-100558 | Junction-99466 | Junction-99467 | 8.66 | 1 | 100 | true | true | 1915 | 9.1408
Pipe-100559 | Junction-99466 | Junction-99083 | 14.52 | 1 | 100 | true | true | 1915 | 9.1408
Pipe-100560 | Junction-99088 | Junction-99466 | 3.75 | 1 | 100 | true | true | 1915 | 9.1408
Pipe-100561 | Junction-99463 | Junction-99089 | 6.71 | 0.217 | 82.5 | true | true | 962 | 4.5919
Pipe-100564 | Junction-99461 | Junction-99462 | 13.88 | 0.217 | 82.5 | true | true | 962 | 4.5919
Pipe-100565 | Junction-99826 | Junction-99461 | 17.93 | 0.217 | 82.5 | true | true | 962 | 4.5919
Pipe-100566 | Junction-55566 | Junction-99438 | 19.88 | 0.282 | 160.3 | true | true | 5533 | 26.4105
Pipe-100567 | Junction-55566 | Junction-99472 | 29.75 | 1 | 100 | true | true | 1915 | 9.1408
Pipe-100568 | Junction-55565 | Junction-99473 | 3.08 | 1 | 100 | true | true | 1915 | 9.1408
Pipe-100577 | Junction-99479 | Junction-10519 | 84.82 | 0.254 | 132.5 | true | true | 3354 | 16.0095
Pipe-100580 | Junction-99479 | Junction-99484 | 66.28 | 0.18 | 54.5 | true | true | 321 | 1.5322
Pipe-100584 | Junction-99485 | Junction-18065 | 1.25 | 0.293 | 210.1 | true | true | 11253 | 53.7136
Pipe-100617 | Junction-99350 | Junction-99803 | 125.91 | 0.259 | 82.5 | true | true | 962 | 4.5919
Pipe-100618 | Junction-99513 | Junction-100337 | 26.81 | 0.217 | 82.5 | true | true | 962 | 4.5919
Pipe-100619 | Junction-99515 | Junction-99513 | 5.17 | 0.217 | 82.5 | true | true | 962 | 4.5919
Pipe-100620 | Junction-99516 | Junction-99517 | 13.97 | 1 | 100 | true | true | 1915 | 9.1408
Pipe-100623 | Junction-98040 | Junction-99519 | 12.78 | 1 | 100 | true | true | 1915 | 9.1408
Pipe-100629 | Junction-99525 | Junction-99526 | 1.59 | 0.217 | 82.5 | true | true | 962 | 4.5919
Pipe-100630 | Junction-99462 | Junction-99463 | 40.01 | 0.217 | 82.5 | true | true | 962 | 4.5919
Pipe-100638 | Junction-1470 | Junction-1472 | 0.43 | 0.156 | 28.5 | true | true | 60 | 0.2864
Pipe-100640 | Junction-37011 | Junction-1475 | 42.87 | 0.633 | 54.5 | true | true | 321 | 1.5322
Pipe-100642 | Junction-99534 | Junction-37011 | 11.1 | 0.18 | 54.5 | true | true | 321 | 1.5322
Pipe-100643 | Junction-99534 | Junction-99535 | 10.65 | 1 | 100 | true | true | 1915 | 9.1408
Pipe-100644 | Junction-99536 | Junction-99534 | 20.98 | 0.18 | 54.5 | true | true | 321 | 1.5322
Pipe-100645 | Junction-99536 | Junction-99537 | 3.41 | 1 | 100 | true | true | 1915 | 9.1408
Pipe-100646 | Junction-99536 | Junction-99538 | 8.48 | 1 | 100 | true | true | 1915 | 9.1408
Pipe-100647 | Junction-99539 | Junction-99536 | 17.77 | 0.18 | 54.5 | true | true | 321 | 1.5322
Pipe-100649 | Junction-99540 | Junction-99542 | 5.58 | 1 | 100 | true | true | 1915 | 9.1408
Pipe-100668 | Junction-99319 | Junction-99559 | 27.19 | 0.18 | 54.5 | true | true | 321 | 1.5322
Pipe-100678 | Junction-18008 | Junction-17277 | 0.15 | 0.166 | 43.1 | true | true | 172 | 0.821
Pipe-100686 | Junction-17277 | Junction-99004 | 60.77 | 0.166 | 43.1 | true | true | 172 | 0.821
Pipe-100718 | Junction-33957 | Junction-99598 | 157.55 | 0.225 | 107.1 | true | true | 1915 | 9.1408
Pipe-100730 | Junction-97934 | Junction-96224 | 252.58 | 0.37 | 210.1 | true | true | 11253 | 53.7136
Pipe-100732 | Junction-99121 | Junction-99613 | 23.29 | 0.134 | 28.5 | true | true | 60 | 0.2864
Pipe-100747 | Junction-99517 | Junction-99625 | 19.74 | 1 | 100 | true | true | 1915 | 9.1408
Pipe-100748 | Junction-99517 | Junction-99515 | 5.75 | 1 | 100 | true | true | 1915 | 9.1408
Pipe-100749 | Junction-99626 | Junction-99627 | 3.86 | 1 | 100 | true | true | 1915 | 9.1408
Pipe-100750 | Junction-99626 | Junction-99628 | 8.15 | 1 | 100 | true | true | 1915 | 9.1408
Pipe-100752 | Junction-99630 | Junction-99626 | 20.15 | 1 | 100 | true | true | 1915 | 9.1408
Pipe-100753 | Junction-99631 | Junction-99632 | 6.7 | 1 | 100 | true | true | 1915 | 9.1408
Pipe-100754 | Junction-99631 | Junction-99630 | 6.75 | 0.217 | 82.5 | true | true | 962 | 4.5919
Pipe-100755 | Junction-99634 | Junction-99635 | 6.56 | 1 | 100 | true | true | 1915 | 9.1408
Pipe-100761 | Junction-99424 | Junction-99376 | 27.52 | 0.217 | 82.5 | true | true | 962 | 4.5919
Pipe-100768 | Junction-97770 | Junction-99645 | 50.43 | 0.134 | 28.5 | true | true | 60 | 0.2864
Pipe-100771 | Junction-99651 | Junction-99647 | 43.35 | 0.166 | 43.1 | true | true | 172 | 0.821
Pipe-100776 | Junction-99651 | Junction-99653 | 6.91 | 0.166 | 43.1 | true | true | 172 | 0.821
Pipe-100778 | Junction-18016 | Junction-99655 | 43.02 | 0.134 | 28.5 | true | true | 60 | 0.2864
Pipe-100789 | Junction-18065 | Junction-19274 | 63.6 | 0.217 | 82.5 | true | true | 962 | 4.5919
Pipe-100796 | Junction-18016 | Junction-98841 | 1.91 | 0.254 | 132.5 | true | true | 3354 | 16.0095
Pipe-100800 | Junction-99671 | Junction-99668 | 10.44 | 0.166 | 43.1 | true | true | 172 | 0.821
Pipe-100821 | Junction-37845 | Junction-98878 | 34.35 | 0.282 | 160.3 | true | true | 5533 | 26.4105
Pipe-100822 | Junction-99690 | Junction-37844 | 7.58 | 0.282 | 160.3 | true | true | 5533 | 26.4105
Pipe-100825 | Junction-99671 | Junction-99693 | 14.21 | 0.248 | 70.3 | true | true | 630 | 3.0072
Pipe-100827 | Junction-99226 | Junction-99671 | 74.26 | 0.248 | 70.3 | true | true | 630 | 3.0072
Pipe-100836 | Junction-99701 | Junction-99226 | 10.87 | 1 | 100 | true | true | 1915 | 9.1408
Pipe-100837 | Junction-99702 | Junction-19194 | 2.42 | 0.282 | 160.3 | true | true | 5533 | 26.4105
Pipe-100862 | Junction-99723 | Junction-54118 | 8.79 | 0.18 | 54.5 | true | true | 321 | 1.5322
Pipe-100864 | Junction-54118 | Junction-99727 | 17.34 | 0.18 | 54.5 | true | true | 321 | 1.5322
Pipe-100879 | Junction-99364 | Junction-99277 | 7.38 | 0.282 | 160.3 | true | true | 5533 | 26.4105
Pipe-100889 | Junction-36476 | Junction-59693 | 1042.01 | 0.411 | 312.7 | true | true | 31872 | 152.1337
Pipe-100899 | Junction-99755 | Junction-127246 | 1.46 | 0.217 | 82.5 | true | true | 962 | 4.5919
Pipe-100900 | Junction-99756 | Junction-99755 | 12.79 | 0.217 | 82.5 | true | true | 962 | 4.5919
Pipe-100901 | Junction-99756 | Junction-99757 | 11.28 | 1 | 100 | true | true | 1915 | 9.1408
Pipe-100904 | Junction-100357 | Junction-99760 | 27.15 | 1 | 100 | true | true | 1915 | 9.1408
Pipe-100940 | Junction-99783 | Junction-99019 | 10.71 | 0.225 | 107.1 | true | true | 1915 | 9.1408
Pipe-100952 | Junction-99133 | Junction-99790 | 17.8 | 0.134 | 28.5 | true | true | 60 | 0.2864
Pipe-100953 | Junction-99133 | Junction-47088 | 27.09 | 0.37 | 210.1 | true | true | 11253 | 53.7136
Pipe-100962 | Junction-99278 | Junction-98765 | 49.41 | 1 | 100 | true | true | 1915 | 9.1408
Pipe-100978 | Junction-99816 | Junction-9548 | 153.94 | 0.248 | 70.3 | true | true | 630 | 3.0072
Pipe-100981 | Junction-99818 | Junction-99816 | 35.73 | 0.213 | 54.5 | true | true | 321 | 1.5322
Pipe-100983 | Junction-75753 | Junction-99819 | 12.87 | 0.166 | 43.1 | true | true | 172 | 0.821
Pipe-100986 | Junction-1396 | Junction-99822 | 51.53 | 1 | 100 | true | true | 1915 | 9.1408
Pipe-100987 | Junction-2360 | Junction-1395 | 63.18 | 0.282 | 160.3 | true | true | 5533 | 26.4105
Pipe-100993 | Junction-99826 | Junction-99827 | 23.13 | 1 | 100 | true | true | 1915 | 9.1408
Pipe-100994 | Junction-99515 | Junction-99826 | 25.89 | 0.217 | 82.5 | true | true | 962 | 4.5919
Pipe-100995 | Junction-99828 | Junction-99756 | 21.62 | 0.217 | 82.5 | true | true | 962 | 4.5919
Pipe-101002 | Junction-99828 | Junction-99073 | 6.73 | 1 | 100 | true | true | 1915 | 9.1408
Pipe-101003 | Junction-64021 | Junction-99828 | 24.06 | 0.217 | 82.5 | true | true | 962 | 4.5919
Pipe-101038 | Junction-2147 | Junction-98860 | 66.42 | 0.282 | 160.3 | true | true | 5533 | 26.4105
Pipe-101045 | Junction-99870 | Junction-99869 | 23.72 | 0.18 | 54.5 | true | true | 321 | 1.5322
Pipe-101047 | Junction-99870 | Junction-99871 | 2.47 | 1 | 100 | true | true | 1915 | 9.1408
Pipe-101048 | Junction-99872 | Junction-99870 | 14.16 | 0.18 | 54.5 | true | true | 321 | 1.5322
Pipe-101049 | Junction-99872 | Junction-99873 | 2.68 | 1 | 100 | true | true | 1915 | 9.1408
Pipe-101050 | Junction-99874 | Junction-99872 | 9.01 | 0.18 | 54.5 | true | true | 321 | 1.5322
Pipe-101051 | Junction-99874 | Junction-99875 | 1.86 | 1 | 100 | true | true | 1915 | 9.1408
Pipe-101052 | Junction-99876 | Junction-99874 | 11.41 | 0.18 | 54.5 | true | true | 321 | 1.5322
Pipe-101053 | Junction-99876 | Junction-99877 | 7.21 | 1 | 100 | true | true | 1915 | 9.1408
Pipe-101054 | Junction-49349 | Junction-99876 | 16.3 | 0.18 | 54.5 | true | true | 321 | 1.5322
Pipe-101055 | Junction-49349 | Junction-99878 | 4.18 | 1 | 100 | true | true | 1915 | 9.1408
Pipe-101056 | Junction-99755 | Junction-49349 | 39.27 | 0.18 | 54.5 | true | true | 321 | 1.5322
Pipe-101058 | Junction-99880 | Junction-99881 | 2.76 | 1 | 100 | true | true | 1915 | 9.1408
Pipe-101061 | Junction-98720 | Junction-99884 | 29 | 0.217 | 82.5 | true | true | 962 | 4.5919
Pipe-101062 | Junction-99884 | Junction-98722 | 13.88 | 0.217 | 82.5 | true | true | 962 | 4.5919
Pipe-101065 | Junction-99884 | Junction-98724 | 31.83 | 0.217 | 82.5 | true | true | 962 | 4.5919
Pipe-101068 | Junction-98724 | Junction-99889 | 5.86 | 0.217 | 82.5 | true | true | 962 | 4.5919
Pipe-101071 | Junction-99890 | Junction-64134 | 35.43 | 0.225 | 107.1 | true | true | 1915 | 9.1408
Pipe-101125 | Junction-99073 | Junction-99936 | 3.5 | 1 | 100 | true | true | 1915 | 9.1408
Pipe-101129 | Junction-54179 | Junction-20761 | 22.45 | 0.411 | 312.7 | true | true | 31872 | 152.1337
Pipe-101140 | Junction-98830 | Junction-100420 | 189.11 | 0.225 | 107.1 | true | true | 1915 | 9.1408
Pipe-101180 | Junction-99048 | Junction-99690 | 61.02 | 0.282 | 160.3 | true | true | 5533 | 26.4105
Pipe-101181 | Junction-99052 | Junction-99048 | 32.11 | 0.282 | 160.3 | true | true | 5533 | 26.4105
Pipe-101199 | Junction-41008 | Junction-99368 | 37.49 | 0.282 | 160.3 | true | true | 5533 | 26.4105
Pipe-101201 | Junction-100287 | Junction-41008 | 2.96 | 0.217 | 82.5 | true | true | 962 | 4.5919
Pipe-101207 | Junction-33432 | Junction-99321 | 45.29 | 0.225 | 107.1 | true | true | 1915 | 9.1408
Pipe-101209 | Junction-99018 | Junction-33431 | 93.77 | 0.355 | 263 | true | true | 20264 | 96.7255
Pipe-101219 | Junction-99278 | Junction-99693 | 169.3 | 0.282 | 160.3 | true | true | 5533 | 26.4105
Pipe-101224 | Junction-99890 | Junction-73296 | 7.77 | 1 | 100 | true | true | 1915 | 9.1408
Pipe-101225 | Junction-99781 | Junction-99890 | 61.87 | 0.225 | 107.1 | true | true | 1915 | 9.1408
Pipe-101227 | Junction-34547 | Junction-99781 | 19.68 | 0.225 | 107.1 | true | true | 1915 | 9.1408
Pipe-101229 | Junction-1396 | Junction-60613 | 67.07 | 0.282 | 160.3 | true | true | 5533 | 26.4105
Pipe-101252 | Junction-100018 | Junction-99525 | 18.62 | 0.217 | 82.5 | true | true | 962 | 4.5919
Pipe-101254 | Junction-74498 | Junction-98926 | 9.14 | 1 | 100 | true | true | 1915 | 9.1408
Pipe-101255 | Junction-100018 | Junction-100019 | 2.93 | 1 | 100 | true | true | 1915 | 9.1408
Pipe-101258 | Junction-99703 | Junction-74498 | 27.61 | 0.217 | 82.5 | true | true | 962 | 4.5919
Pipe-101272 | Junction-45717 | Junction-99330 | 28.49 | 0.217 | 82.5 | true | true | 962 | 4.5919
Pipe-101281 | Junction-100035 | Junction-99528 | 9.39 | 0.134 | 28.5 | true | true | 60 | 0.2864
Pipe-101283 | Junction-100035 | Junction-97775 | 29.04 | 1 | 100 | true | true | 1915 | 9.1408
Pipe-101291 | Junction-99690 | Junction-100042 | 8 | 1 | 100 | true | true | 1915 | 9.1408
Pipe-101302 | Junction-100050 | Junction-99974 | 8.58 | 0.282 | 160.3 | true | true | 5533 | 26.4105
Pipe-101303 | Junction-100050 | Junction-100052 | 12.8 | 1 | 100 | true | true | 1915 | 9.1408
Pipe-101307 | Junction-99115 | Junction-100050 | 48.28 | 0.37 | 210.1 | true | true | 11253 | 53.7136
Pipe-101308 | Junction-99115 | Junction-100054 | 11.08 | 1 | 100 | true | true | 1915 | 9.1408
Pipe-101311 | Junction-99395 | Junction-99114 | 47.62 | 0.37 | 210.1 | true | true | 11253 | 53.7136
Pipe-101313 | Junction-99395 | Junction-100058 | 21.06 | 1 | 100 | true | true | 1915 | 9.1408
Pipe-101351 | Junction-2147 | Junction-100035 | 79.43 | 1 | 100 | true | true | 1915 | 9.1408
Pipe-101354 | Junction-100086 | Junction-100403 | 48.43 | 1 | 100 | true | true | 1915 | 9.1408
Pipe-101356 | Junction-100094 | Junction-100086 | 117.81 | 1 | 100 | true | true | 1915 | 9.1408
Pipe-101362 | Junction-100097 | Junction-100096 | 9.47 | 1 | 100 | true | true | 1915 | 9.1408
Pipe-101364 | Junction-100097 | Junction-100098 | 4.18 | 1 | 100 | true | true | 1915 | 9.1408
Pipe-101365 | Junction-100094 | Junction-100097 | 22.98 | 1 | 100 | true | true | 1915 | 9.1408
Pipe-101367 | Junction-100100 | Junction-100094 | 33.74 | 1 | 100 | true | true | 1915 | 9.1408
Pipe-101369 | Junction-99593 | Junction-100102 | 17.3 | 0.134 | 28.5 | true | true | 60 | 0.2864
Pipe-101370 | Junction-99593 | Junction-100103 | 4.37 | 0.134 | 28.5 | true | true | 60 | 0.2864
Pipe-101371 | Junction-1512 | Junction-100104 | 24.97 | 1 | 100 | true | true | 1915 | 9.1408
Pipe-101372 | Junction-1512 | Junction-100105 | 23.63 | 1 | 100 | true | true | 1915 | 9.1408
Pipe-101374 | Junction-100110 | Junction-100107 | 43.2 | 1 | 100 | true | true | 1915 | 9.1408
Pipe-101378 | Junction-100110 | Junction-100111 | 3.67 | 1 | 100 | true | true | 1915 | 9.1408
Pipe-101388 | Junction-100121 | Junction-100156 | 137.1 | 0.24 | 70.3 | true | true | 630 | 3.0072
Pipe-101396 | Junction-99304 | Junction-100124 | 43.3 | 0.166 | 43.1 | true | true | 172 | 0.821
Pipe-101454 | Junction-98936 | Junction-100168 | 31.54 | 0.18 | 54.5 | true | true | 321 | 1.5322
Pipe-101464 | Junction-9981 | Junction-19268 | 199.1 | 0.293 | 210.1 | true | true | 11253 | 53.7136
Pipe-101469 | Junction-61093 | Junction-100172 | 31.14 | 0.191 | 43.1 | true | true | 172 | 0.821
Pipe-101475 | Junction-2228 | Junction-61093 | 106.16 | 0.248 | 70.3 | true | true | 630 | 3.0072
Pipe-101479 | Junction-40791 | Junction-100179 | 8.79 | 1 | 100 | true | true | 1915 | 9.1408
Pipe-101538 | Junction-100224 | Junction-100220 | 68.93 | 1 | 100 | true | true | 1915 | 9.1408
Pipe-101543 | Junction-100224 | Junction-100227 | 8.07 | 1 | 100 | true | true | 1915 | 9.1408
Pipe-101544 | Junction-100228 | Junction-100224 | 6.36 | 1 | 100 | true | true | 1915 | 9.1408
Pipe-101545 | Junction-100228 | Junction-100229 | 2.74 | 1 | 100 | true | true | 1915 | 9.1408
Pipe-101546 | Junction-100225 | Junction-100228 | 9.37 | 1 | 100 | true | true | 1915 | 9.1408
Pipe-101548 | Junction-19192 | Junction-100225 | 50.98 | 0.282 | 160.3 | true | true | 5533 | 26.4105
Pipe-101549 | Junction-19192 | Junction-100231 | 3.99 | 1 | 100 | true | true | 1915 | 9.1408
Pipe-101559 | Junction-100239 | Junction-99783 | 21.58 | 0.225 | 107.1 | true | true | 1915 | 9.1408
Pipe-101561 | Junction-1513 | Junction-100240 | 8.77 | 1 | 100 | true | true | 1915 | 9.1408
Pipe-101562 | Junction-1513 | Junction-100241 | 0.87 | 1 | 100 | true | true | 1915 | 9.1408
Pipe-101565 | Junction-99723 | Junction-98919 | 126.18 | 0.166 | 43.1 | true | true | 172 | 0.821
Pipe-101570 | Junction-6710 | Junction-100245 | 9.97 | 1 | 100 | true | true | 1915 | 9.1408
Pipe-101571 | Junction-6710 | Junction-100039 | 5.13 | 0.156 | 28.5 | true | true | 60 | 0.2864
Pipe-101572 | Junction-100246 | Junction-6710 | 26.42 | 0.18 | 54.5 | true | true | 321 | 1.5322
Pipe-101573 | Junction-100246 | Junction-100247 | 2.1 | 1 | 100 | true | true | 1915 | 9.1408
Pipe-101574 | Junction-99869 | Junction-100246 | 8.33 | 0.18 | 54.5 | true | true | 321 | 1.5322
Pipe-101575 | Junction-99869 | Junction-100249 | 9.14 | 1 | 100 | true | true | 1915 | 9.1408
Pipe-101597 | Junction-99830 | Junction-33957 | 5.15 | 0.225 | 107.1 | true | true | 1915 | 9.1408
Pipe-101598 | Junction-2042 | Junction-100261 | 14.03 | 0.213 | 54.5 | true | true | 321 | 1.5322
Pipe-101599 | Junction-99526 | Junction-100262 | 5.39 | 1 | 100 | true | true | 1915 | 9.1408
Pipe-101601 | Junction-100266 | Junction-100264 | 55.21 | 1 | 100 | true | true | 1915 | 9.1408
Pipe-101603 | Junction-100266 | Junction-100267 | 5.49 | 1 | 100 | true | true | 1915 | 9.1408
Pipe-101604 | Junction-30414 | Junction-100266 | 34.36 | 1 | 100 | true | true | 1915 | 9.1408
Pipe-101607 | Junction-99048 | Junction-100043 | 119.21 | 1 | 100 | true | true | 1915 | 9.1408
Pipe-101608 | Junction-98926 | Junction-100269 | 1.61 | 1 | 100 | true | true | 1915 | 9.1408
Pipe-101613 | Junction-100272 | Junction-100273 | 1.73 | 1 | 100 | true | true | 1915 | 9.1408
Pipe-101614 | Junction-100274 | Junction-100272 | 17.16 | 0.18 | 54.5 | true | true | 321 | 1.5322
Pipe-101615 | Junction-100274 | Junction-100275 | 5.73 | 1 | 100 | true | true | 1915 | 9.1408
Pipe-101616 | Junction-99539 | Junction-100274 | 14.95 | 0.18 | 54.5 | true | true | 321 | 1.5322
Pipe-101618 | Junction-100277 | Junction-99539 | 30.34 | 0.217 | 82.5 | true | true | 962 | 4.5919
Pipe-101619 | Junction-100277 | Junction-100278 | 9.85 | 1 | 100 | true | true | 1915 | 9.1408
Pipe-101632 | Junction-100245 | Junction-100288 | 16.45 | 1 | 100 | true | true | 1915 | 9.1408
Pipe-101633 | Junction-100245 | Junction-100289 | 9.3 | 1 | 100 | true | true | 1915 | 9.1408
Pipe-101634 | Junction-100290 | Junction-100291 | 5.17 | 1 | 100 | true | true | 1915 | 9.1408
Pipe-101635 | Junction-100292 | Junction-100293 | 16.81 | 1 | 100 | true | true | 1915 | 9.1408
Pipe-101636 | Junction-100294 | Junction-100295 | 26.26 | 1 | 100 | true | true | 1915 | 9.1408
Pipe-101637 | Junction-100296 | Junction-100297 | 4.52 | 1 | 100 | true | true | 1915 | 9.1408
Pipe-101638 | Junction-100298 | Junction-100299 | 2.87 | 1 | 100 | true | true | 1915 | 9.1408
Pipe-101639 | Junction-100300 | Junction-100301 | 11.78 | 1 | 100 | true | true | 1915 | 9.1408
Pipe-101640 | Junction-100300 | Junction-100303 | 2.89 | 1 | 100 | true | true | 1915 | 9.1408
Pipe-101642 | Junction-100298 | Junction-100300 | 11.1 | 1 | 100 | true | true | 1915 | 9.1408
Pipe-101643 | Junction-100296 | Junction-100298 | 20.23 | 1 | 100 | true | true | 1915 | 9.1408
Pipe-101645 | Junction-100294 | Junction-100305 | 9.39 | 1 | 100 | true | true | 1915 | 9.1408
Pipe-101659 | Junction-99032 | Junction-99651 | 2.44 | 0.18 | 54.5 | true | true | 321 | 1.5322
Pipe-101669 | Junction-99032 | Junction-65389 | 58.96 | 0.225 | 107.1 | true | true | 1915 | 9.1408
Pipe-101671 | Junction-99032 | Junction-98830 | 62.29 | 0.225 | 107.1 | true | true | 1915 | 9.1408
Pipe-101672 | Junction-98922 | Junction-37885 | 11.48 | 0.225 | 107.1 | true | true | 1915 | 9.1408
Pipe-101676 | Junction-98922 | Junction-99723 | 83.66 | 0.205 | 70.3 | true | true | 630 | 3.0072
Pipe-101682 | Junction-100332 | Junction-100333 | 5.99 | 1 | 100 | true | true | 1915 | 9.1408
Pipe-101683 | Junction-99703 | Junction-100332 | 20.67 | 1 | 100 | true | true | 1915 | 9.1408
Pipe-101684 | Junction-99330 | Junction-100334 | 7.26 | 1 | 100 | true | true | 1915 | 9.1408
Pipe-101685 | Junction-45717 | Junction-100335 | 9.15 | 1 | 100 | true | true | 1915 | 9.1408
Pipe-101686 | Junction-99889 | Junction-100336 | 9.83 | 1 | 100 | true | true | 1915 | 9.1408
Pipe-101687 | Junction-100337 | Junction-100338 | 9.02 | 1 | 100 | true | true | 1915 | 9.1408
Pipe-101688 | Junction-98717 | Junction-100339 | 2.52 | 1 | 100 | true | true | 1915 | 9.1408
Pipe-101689 | Junction-98719 | Junction-100340 | 1.58 | 1 | 100 | true | true | 1915 | 9.1408
Pipe-101693 | Junction-99974 | Junction-99121 | 49.97 | 0.166 | 43.1 | true | true | 172 | 0.821
Pipe-101696 | Junction-100290 | Junction-100292 | 2.4 | 1 | 100 | true | true | 1915 | 9.1408
Pipe-101710 | Junction-100332 | Junction-100357 | 8.72 | 1 | 100 | true | true | 1915 | 9.1408
Pipe-101711 | Junction-100359 | Junction-41620 | 56.98 | 1 | 100 | true | true | 1915 | 9.1408
Pipe-101716 | Junction-16278 | Junction-100359 | 13.93 | 0.217 | 82.5 | true | true | 962 | 4.5919
Pipe-101725 | Junction-97937 | Junction-9492 | 0.98 | 1 | 100 | true | true | 1915 | 9.1408
Pipe-101726 | Junction-99110 | Junction-97937 | 1.23 | 1 | 100 | true | true | 1915 | 9.1408
Pipe-101728 | Junction-100368 | Junction-18027 | 23.81 | 0.306 | 132.5 | true | true | 3354 | 16.0095
Pipe-101731 | Junction-9548 | Junction-100368 | 156.01 | 0.248 | 70.3 | true | true | 630 | 3.0072
Pipe-101744 | Junction-100381 | Junction-100382 | 3.18 | 1 | 100 | true | true | 1915 | 9.1408
Pipe-101745 | Junction-99974 | Junction-100381 | 54.77 | 0.37 | 210.1 | true | true | 11253 | 53.7136
Pipe-101747 | Junction-99693 | Junction-55565 | 212.46 | 0.282 | 160.3 | true | true | 5533 | 26.4105
Pipe-101755 | Junction-33432 | Junction-100388 | 10.78 | 0.293 | 210.1 | true | true | 11253 | 53.7136
Pipe-101760 | Junction-99326 | Junction-69578 | 57.84 | 0.217 | 82.5 | true | true | 962 | 4.5919
Pipe-101774 | Junction-99630 | Junction-98722 | 34.46 | 0.217 | 82.5 | true | true | 962 | 4.5919
Pipe-101776 | Junction-100337 | Junction-99631 | 24.48 | 0.217 | 82.5 | true | true | 962 | 4.5919
Pipe-101780 | Junction-100239 | Junction-100402 | 81.12 | 1 | 100 | true | true | 1915 | 9.1408
Pipe-101781 | Junction-100086 | Junction-100239 | 63.4 | 1 | 100 | true | true | 1915 | 9.1408
Pipe-101812 | Junction-75387 | Junction-75752 | 41.76 | 0.18 | 54.5 | true | true | 321 | 1.5322
Pipe-101816 | Junction-100420 | Junction-75386 | 76.82 | 0.217 | 82.5 | true | true | 962 | 4.5919
Pipe-101824 | Junction-100292 | Junction-100294 | 32.33 | 1 | 100 | true | true | 1915 | 9.1408
Pipe-101825 | Junction-99760 | Junction-100290 | 5.33 | 1 | 100 | true | true | 1915 | 9.1408
Pipe-101846 | Junction-98723 | Junction-100436 | 9.25 | 1 | 100 | true | true | 1915 | 9.1408
Pipe-101847 | Junction-98723 | Junction-100437 | 6.83 | 1 | 100 | true | true | 1915 | 9.1408
Pipe-101848 | Junction-100336 | Junction-100438 | 6.69 | 1 | 100 | true | true | 1915 | 9.1408
Pipe-101849 | Junction-100336 | Junction-100439 | 9.7 | 1 | 100 | true | true | 1915 | 9.1408
Pipe-101850 | Junction-100440 | Junction-100441 | 2.16 | 1 | 100 | true | true | 1915 | 9.1408
Pipe-101851 | Junction-100440 | Junction-100442 | 3.58 | 1 | 100 | true | true | 1915 | 9.1408
Pipe-101852 | Junction-100305 | Junction-100440 | 17.73 | 1 | 100 | true | true | 1915 | 9.1408
Pipe-101853 | Junction-100305 | Junction-100296 | 9.27 | 1 | 100 | true | true | 1915 | 9.1408
Pipe-101854 | Junction-99760 | Junction-100443 | 19.37 | 1 | 100 | true | true | 1915 | 9.1408
Pipe-101855 | Junction-100357 | Junction-100444 | 25.24 | 1 | 100 | true | true | 1915 | 9.1408
Pipe-102854 | Sarfvik | Junction-6737 | 370.59 | 0.404 | 393.8 | true | true | 58221 | 277.9045
Pipe-102913 | Junction-101660 | Junction-58617 | 2.63 | 0.282 | 160.3 | true | true | 5533 | 26.4105
Pipe-102920 | Junction-101660 | Ericsson | 4.84 | 0.282 | 160.3 | false | true | 5533 | 26.4105
Pipe-103402 | Junction-102990 | Junction-3673 | 91.11 | 0.436 | 160.3 | true | true | 5533 | 26.4105
Pipe-103758 | Junction-9808 | Junction-103455 | 428.02 | 0.225 | 107.1 | true | true | 1915 | 9.1408
Pipe-103760 | Junction-102036 | Junction-102637 | 5.78 | 0.134 | 28.5 | true | true | 60 | 0.2864
Pipe-104142 | Junction-101919 | Junction-102990 | 33.98 | 0.282 | 160.3 | true | true | 5533 | 26.4105
Pipe-104469 | Junction-103322 | Junction-103293 | 10.79 | 0.166 | 43.1 | true | true | 172 | 0.821
Pipe-104496 | Junction-103455 | Junction-103313 | 66.62 | 0.217 | 82.5 | true | true | 962 | 4.5919
Pipe-104517 | Junction-102277 | Junction-103322 | 179.32 | 0.205 | 70.3 | true | true | 630 | 3.0072
Pipe-104734 | Junction-102036 | Junction-48688 | 7 | 0.225 | 107.1 | true | true | 1915 | 9.1408
Pipe-104735 | Junction-102277 | Junction-95215 | 6.8 | 0.303 | 107.1 | true | true | 1915 | 9.1408
Pipe-106599 | Junction-105140 | Junction-105118 | 64.31 | 0.166 | 43.1 | true | true | 172 | 0.821
Pipe-106740 | Junction-105274 | Junction-50281 | 35.51 | 0.18 | 54.5 | true | true | 321 | 1.5322
Pipe-106870 | Junction-30008 | Junction-105411 | 6.18 | 0.259 | 82.5 | true | true | 962 | 4.5919
Pipe-106999 | Junction-105540 | Junction-1036 | 25.02 | 0.293 | 210.1 | true | true | 11253 | 53.7136
Pipe-107007 | Junction-105560 | Junction-105543 | 61.46 | 0.166 | 43.1 | true | true | 172 | 0.821
Pipe-107018 | Junction-105560 | Junction-101919 | 0.73 | 0.436 | 160.3 | true | true | 5533 | 26.4105
Pipe-107032 | Junction-1455 | Junction-105562 | 30.37 | 0.134 | 28.5 | true | true | 60 | 0.2864
Pipe-107262 | Junction-105811 | Junction-105810 | 1.4 | 0.633 | 54.5 | true | true | 321 | 1.5322
Pipe-107263 | Junction-105812 | Junction-105813 | 0.64 | 0.633 | 54.5 | true | true | 321 | 1.5322
Pipe-107264 | Junction-105812 | Junction-105811 | 0.31 | 0.661 | 70.3 | true | true | 630 | 3.0072
Pipe-107265 | Junction-105814 | Junction-105812 | 0.91 | 0.661 | 70.3 | true | true | 630 | 3.0072
Pipe-107272 | Junction-105540 | Junction-105814 | 48.42 | 0.205 | 70.3 | true | true | 630 | 3.0072
Pipe-107523 | Junction-106048 | Junction-106045 | 6.96 | 0.166 | 43.1 | true | true | 172 | 0.821
Pipe-107532 | Junction-106055 | Junction-41284 | 9.01 | 0.166 | 43.1 | true | true | 172 | 0.821
Pipe-107551 | Junction-106055 | Junction-106057 | 123.6 | 0.254 | 132.5 | true | true | 3354 | 16.0095
Pipe-107556 | Junction-106048 | Junction-106055 | 26.17 | 0.254 | 132.5 | true | true | 3354 | 16.0095
Pipe-107559 | Junction-106088 | Junction-106048 | 44.64 | 0.254 | 132.5 | true | true | 3354 | 16.0095
Pipe-107568 | Junction-106092 | Junction-106090 | 21.99 | 0.18 | 54.5 | true | true | 321 | 1.5322
Pipe-107571 | Junction-106092 | Junction-35794 | 10.52 | 0.355 | 263 | true | true | 20264 | 96.7255
Pipe-107814 | Junction-106326 | Junction-106327 | 1.7 | 0.205 | 70.3 | true | true | 630 | 3.0072
Pipe-108032 | Junction-106326 | Junction-106501 | 1.71 | 0.205 | 70.3 | true | true | 630 | 3.0072
Pipe-108035 | Junction-106504 | Junction-106326 | 61.48 | 0.205 | 70.3 | true | true | 630 | 3.0072
Pipe-108037 | Junction-106504 | Junction-35760 | 38.2 | 0.355 | 263 | true | true | 20264 | 96.7255
Pipe-108042 | Junction-107214 | Junction-106507 | 70.54 | 0.166 | 43.1 | true | true | 172 | 0.821
Pipe-108299 | Junction-907 | Junction-106088 | 2.38 | 0.282 | 160.3 | true | true | 5533 | 26.4105
Pipe-108313 | Junction-1044 | Junction-105540 | 2.26 | 0.293 | 210.1 | true | true | 11253 | 53.7136
Pipe-109052 | Junction-105140 | Junction-16565 | 57.24 | 0.217 | 82.5 | true | true | 962 | 4.5919
Pipe-109073 | Junction-20377 | Junction-105140 | 188.92 | 0.217 | 82.5 | true | true | 962 | 4.5919
Pipe-109294 | Junction-31990 | Junction-106092 | 28.97 | 0.355 | 263 | true | true | 20264 | 96.7255
Pipe-109301 | Junction-35794 | Junction-106504 | 130.45 | 0.355 | 263 | true | true | 20264 | 96.7255
Pipe-109372 | Junction-107214 | Junction-25543 | 40.58 | 0.355 | 263 | true | true | 20264 | 96.7255
Pipe-109543 | Junction-35760 | Junction-107214 | 50.72 | 0.355 | 263 | true | true | 20264 | 96.7255
Pipe-109608 | Junction-50281 | Junction-50282 | 6.87 | 0.18 | 54.5 | true | true | 321 | 1.5322
Pipe-110786 | Junction-917 | Junction-97180 | 18.45 | 0.436 | 160.3 | true | true | 5533 | 26.4105
Pipe-110804 | Junction-50282 | Junction-97770 | 8.12 | 0.18 | 54.5 | true | true | 321 | 1.5322
Pipe-110833 | Junction-1704 | Junction-106057 | 52.22 | 0.436 | 160.3 | true | true | 5533 | 26.4105
Pipe-110839 | Junction-106045 | Junction-98228 | 104.81 | 0.191 | 43.1 | true | true | 172 | 0.821
Pipe-110855 | Junction-97180 | Junction-97898 | 115.74 | 0.191 | 43.1 | true | true | 172 | 0.821
Pipe-110904 | Junction-99237 | Junction-105274 | 4.52 | 0.205 | 70.3 | true | true | 630 | 3.0072
Pipe-110907 | Junction-99375 | Junction-99373 | 18.4 | 1 | 100 | true | true | 1915 | 9.1408
Pipe-110928 | Junction-99375 | Junction-99634 | 104.25 | 0.217 | 82.5 | true | true | 962 | 4.5919
Pipe-110929 | Junction-99376 | Junction-99375 | 51.84 | 0.217 | 82.5 | true | true | 962 | 4.5919
Pipe-110935 | Junction-97770 | Junction-99866 | 65.93 | 0.18 | 54.5 | true | true | 321 | 1.5322
Pipe-110945 | Junction-99111 | Junction-105276 | 0.57 | 0.282 | 160.3 | true | true | 5533 | 26.4105
Pipe-110953 | Junction-105282 | Junction-99237 | 26.01 | 0.205 | 70.3 | true | true | 630 | 3.0072
Pipe-110957 | Junction-105276 | Junction-105282 | 58.08 | 0.217 | 82.5 | true | true | 962 | 4.5919
Pipe-112019 | Junction-20237 | Junction-20656 | 73.26 | 0.71 | 107.1 | true | true | 1915 | 9.1408
Pipe-112026 | Junction-18900 | Junction-20691 | 72.56 | 0.775 | 132.5 | true | true | 3354 | 16.0095
Pipe-114188 | Junction-111147 | Junction-111142 | 4.76 | 0.18 | 54.5 | true | true | 321 | 1.5322
Pipe-114194 | Junction-111155 | Junction-111150 | 2.01 | 0.18 | 54.5 | true | true | 321 | 1.5322
Pipe-114199 | Junction-111155 | Junction-27084 | 8.59 | 0.217 | 82.5 | true | true | 962 | 4.5919
Pipe-114207 | Junction-111157 | Junction-111160 | 25.52 | 0.205 | 70.3 | true | true | 630 | 3.0072
Pipe-114222 | Junction-111193 | Junction-111171 | 51.35 | 0.166 | 43.1 | true | true | 172 | 0.821
Pipe-114238 | Junction-111208 | Junction-111196 | 27.27 | 0.217 | 82.5 | true | true | 962 | 4.5919
Pipe-114253 | Junction-111223 | Junction-111213 | 25.98 | 0.18 | 54.5 | true | true | 321 | 1.5322
Pipe-114272 | Junction-111225 | Junction-111228 | 28.96 | 0.18 | 54.5 | true | true | 321 | 1.5322
Pipe-116043 | Junction-3224 | Junction-3165 | 71.84 | 0.254 | 132.5 | true | true | 3354 | 16.0095
Pipe-116102 | Junction-4076 | Junction-111157 | 10.66 | 0.364 | 132.5 | true | true | 3354 | 16.0095
Pipe-116287 | Junction-7442 | Junction-111223 | 19.48 | 0.217 | 82.5 | true | true | 962 | 4.5919
Pipe-116488 | Junction-165 | Junction-111193 | 266.4 | 0.217 | 82.5 | true | true | 962 | 4.5919
Pipe-116559 | Junction-111208 | Junction-9986 | 71.36 | 0.217 | 82.5 | true | true | 962 | 4.5919
Pipe-117067 | Junction-22022 | Junction-111147 | 114.11 | 0.217 | 82.5 | true | true | 962 | 4.5919
Pipe-117218 | Junction-48688 | Junction-111155 | 98.46 | 0.217 | 82.5 | true | true | 962 | 4.5919
Pipe-117591 | Junction-116686 | Junction-13700 | 284.46 | 0.411 | 312.7 | true | true | 31872 | 152.1337
Pipe-117600 | Junction-114744 | Junction-34334 | 63.91 | 0.205 | 70.3 | true | true | 630 | 3.0072
Pipe-117629 | Junction-37303 | Junction-114744 | 98.48 | 0.205 | 70.3 | true | true | 630 | 3.0072
Pipe-117658 | Junction-114781 | Junction-42173 | 16.02 | 1 | 100 | true | true | 1915 | 9.1408
Pipe-118053 | Junction-37596 | Junction-115208 | 30.08 | 0.254 | 132.5 | true | true | 3354 | 16.0095
Pipe-118486 | Junction-48315 | Junction-115682 | 14.2 | 0.18 | 54.5 | true | true | 321 | 1.5322
Pipe-118794 | Junction-111225 | Junction-14261 | 256.98 | 0.404 | 393.8 | true | true | 58221 | 277.9045
Pipe-119816 | Junction-97180 | Junction-9062 | 105.82 | 0.436 | 160.3 | true | true | 5533 | 26.4105
Pipe-119915 | Junction-98710 | Junction-34444 | 40.17 | 0.411 | 312.7 | true | true | 31872 | 152.1337
Pipe-119922 | Junction-114781 | Junction-72630 | 47.41 | 0.217 | 82.5 | true | true | 962 | 4.5919
Pipe-119924 | Junction-71596 | Junction-114781 | 93.83 | 0.217 | 82.5 | true | true | 962 | 4.5919
Pipe-119990 | Junction-111157 | Junction-98397 | 25.59 | 0.364 | 132.5 | true | true | 3354 | 16.0095
Pipe-120033 | Junction-127246 | Junction-99880 | 30.33 | 0.217 | 82.5 | true | true | 962 | 4.5919
Pipe-120063 | Junction-99019 | Junction-98710 | 321.92 | 0.293 | 210.1 | true | true | 11253 | 53.7136
Pipe-120068 | Junction-10018 | Junction-100110 | 158.15 | 0.217 | 82.5 | true | true | 962 | 4.5919
Pipe-120080 | Junction-116891 | Junction-116892 | 65.78 | 0.9 | 263 | true | true | 20264 | 96.7255
Pipe-120081 | Junction-97934 | Junction-99438 | 76.57 | 0.282 | 160.3 | true | true | 5533 | 26.4105
Pipe-120088 | Junction-100287 | Junction-99111 | 144.27 | 0.282 | 160.3 | true | true | 5533 | 26.4105
Pipe-120098 | Junction-116901 | Junction-116891 | 44.61 | 0.355 | 263 | true | true | 20264 | 96.7255
Pipe-120100 | Junction-9556 | Junction-116901 | 54.6 | 0.355 | 263 | true | true | 20264 | 96.7255
Pipe-120820 | Junction-115208 | Junction-117566 | 45.04 | 0.18 | 54.5 | true | true | 321 | 1.5322
Pipe-120849 | Junction-114744 | Junction-117594 | 32.66 | 0.166 | 43.1 | true | true | 172 | 0.821
Pipe-120881 | Junction-14297 | Junction-23736 | 225.09 | 0.205 | 70.3 | true | true | 630 | 3.0072
Pipe-121410 | Junction-116686 | Junction-118160 | 46.88 | 0.18 | 54.5 | true | true | 321 | 1.5322
Pipe-121429 | Junction-116901 | Junction-118151 | 9.55 | 0.166 | 43.1 | true | true | 172 | 0.821
Pipe-123841 | Junction-116892 | Junction-2040 | 30.12 | 0.355 | 263 | true | true | 20264 | 96.7255
Pipe-123846 | Junction-115208 | Junction-36469 | 268.71 | 0.254 | 132.5 | true | true | 3354 | 16.0095
Pipe-123849 | Junction-111147 | Junction-21644 | 112.51 | 0.217 | 82.5 | true | true | 962 | 4.5919
Pipe-123857 | Junction-111193 | Junction-8165 | 292.58 | 0.217 | 82.5 | true | true | 962 | 4.5919
Pipe-123862 | Junction-97373 | Junction-98243 | 241.39 | 0.364 | 132.5 | true | true | 3354 | 16.0095
Pipe-124597 | Junction-120722 | Junction-120721 | 0.65 | 0.254 | 132.5 | true | true | 3354 | 16.0095
Pipe-124743 | Junction-120721 | Junction-120847 | 4.55 | 0.217 | 82.5 | true | true | 962 | 4.5919
Pipe-126196 | Junction-120847 | Junction-97753 | 5.36 | 0.259 | 82.5 | true | true | 962 | 4.5919
Pipe-127195 | Junction-122930 | Junction-34033 | 22.79 | 0.355 | 263 | true | true | 20264 | 96.7255
Pipe-131360 | Junction-126962 | Junction-127158 | 236.94 | 0.205 | 70.3 | true | true | 630 | 3.0072
Pipe-131566 | Junction-127162 | Junction-127160 | 2.46 | 0.166 | 43.1 | true | true | 172 | 0.821
Pipe-131569 | Junction-127162 | Junction-127164 | 2.38 | 0.217 | 82.5 | true | true | 962 | 4.5919
Pipe-131572 | Junction-127171 | Junction-127162 | 2.23 | 0.217 | 82.5 | true | true | 962 | 4.5919
Pipe-131577 | Junction-127164 | Junction-99010 | 31.19 | 0.259 | 82.5 | true | true | 962 | 4.5919
Pipe-131578 | Junction-127181 | Junction-127174 | 16.79 | 0.166 | 43.1 | true | true | 172 | 0.821
Pipe-131583 | Junction-127181 | Junction-127182 | 0.41 | 0.205 | 70.3 | true | true | 630 | 3.0072
Pipe-131587 | Junction-127182 | Junction-127184 | 11.5 | 0.18 | 54.5 | true | true | 321 | 1.5322
Pipe-131601 | Junction-127197 | Junction-127181 | 1.8 | 0.205 | 70.3 | true | true | 630 | 3.0072
Pipe-131613 | Junction-127219 | Junction-127208 | 21.95 | 0.18 | 54.5 | true | true | 321 | 1.5322
Pipe-131624 | Junction-127234 | Junction-127222 | 68.73 | 0.18 | 54.5 | true | true | 321 | 1.5322
Pipe-131630 | Junction-128253 | Junction-127246 | 10.08 | 0.134 | 28.5 | true | true | 60 | 0.2864
Pipe-131640 | Junction-127265 | Junction-128234 | 49.54 | 0.18 | 54.5 | true | true | 321 | 1.5322
Pipe-131670 | Junction-127291 | Junction-98264 | 32.79 | 0.191 | 43.1 | true | true | 172 | 0.821
Pipe-131675 | Junction-127300 | Junction-127293 | 32.67 | 0.166 | 43.1 | true | true | 172 | 0.821
Pipe-131686 | Junction-127332 | Junction-127302 | 42.84 | 0.18 | 54.5 | true | true | 321 | 1.5322
Pipe-131690 | Junction-127314 | Junction-127291 | 12.34 | 0.18 | 54.5 | true | true | 321 | 1.5322
Pipe-131720 | Junction-127376 | Junction-127340 | 69.56 | 0.18 | 54.5 | true | true | 321 | 1.5322
Pipe-131751 | Junction-127376 | Junction-127332 | 92.18 | 0.404 | 393.8 | true | true | 58221 | 277.9045
Pipe-131752 | Junction-127378 | Junction-127442 | 20.16 | 0.205 | 70.3 | true | true | 630 | 3.0072
Pipe-131753 | Junction-127380 | Junction-127378 | 1.64 | 0.205 | 70.3 | true | true | 630 | 3.0072
Pipe-131754 | Junction-127383 | Junction-127382 | 7.02 | 0.225 | 107.1 | true | true | 1915 | 9.1408
Pipe-131757 | Junction-127386 | Junction-127385 | 2.61 | 0.225 | 107.1 | true | true | 1915 | 9.1408
Pipe-131758 | Junction-127387 | Junction-127383 | 0.89 | 0.282 | 160.3 | true | true | 5533 | 26.4105
Pipe-131759 | Junction-127387 | Junction-127386 | 0.88 | 0.282 | 160.3 | true | true | 5533 | 26.4105
Pipe-131778 | Junction-127406 | Junction-127387 | 3.33 | 0.282 | 160.3 | true | true | 5533 | 26.4105
Pipe-131780 | Junction-127924 | Junction-99593 | 12.4 | 0.166 | 43.1 | true | true | 172 | 0.821
Pipe-131781 | Junction-127409 | Junction-127410 | 12.55 | 0.585 | 28.5 | true | true | 60 | 0.2864
Pipe-131782 | Junction-127411 | Junction-100427 | 17.97 | 0.156 | 28.5 | true | true | 60 | 0.2864
Pipe-131783 | Junction-127412 | Junction-127413 | 4.97 | 0.585 | 28.5 | true | true | 60 | 0.2864
Pipe-131784 | Junction-127414 | Junction-100277 | 19.55 | 0.217 | 82.5 | true | true | 962 | 4.5919
Pipe-131806 | Junction-127438 | Junction-127417 | 13.76 | 0.205 | 70.3 | true | true | 630 | 3.0072
Pipe-131808 | Junction-127442 | Junction-127438 | 15.41 | 0.205 | 70.3 | true | true | 630 | 3.0072
Pipe-131813 | Junction-127446 | Junction-127380 | 12.62 | 0.205 | 70.3 | true | true | 630 | 3.0072
Pipe-131816 | Junction-127380 | Junction-127411 | 7.06 | 0.134 | 28.5 | true | true | 60 | 0.2864
Pipe-131835 | Junction-127378 | Junction-127464 | 4.67 | 0.134 | 28.5 | true | true | 60 | 0.2864
Pipe-131864 | Junction-127442 | Junction-127493 | 13.5 | 0.134 | 28.5 | true | true | 60 | 0.2864
Pipe-131870 | Junction-127438 | Junction-127412 | 1.42 | 0.134 | 28.5 | true | true | 60 | 0.2864
Pipe-131874 | Junction-127417 | Junction-127414 | 8.08 | 0.205 | 70.3 | true | true | 630 | 3.0072
Pipe-131882 | Junction-127510 | Junction-127300 | 2.3 | 0.18 | 54.5 | true | true | 321 | 1.5322
Pipe-131889 | Junction-127514 | Junction-127516 | 3.6 | 0.291 | 263 | true | true | 20264 | 96.7255
Pipe-131905 | Junction-127533 | Junction-127514 | 0.94 | 0.291 | 263 | true | true | 20264 | 96.7255
Pipe-131906 | Junction-127534 | Junction-127516 | 0.68 | 0.355 | 263 | true | true | 20264 | 96.7255
Pipe-131909 | Junction-127537 | Junction-127538 | 0.6 | 0.134 | 28.5 | true | true | 60 | 0.2864
Pipe-131913 | Junction-128246 | Junction-127537 | 14.56 | 0.166 | 43.1 | true | true | 172 | 0.821
Pipe-131963 | Junction-127417 | Junction-127596 | 16.34 | 0.134 | 28.5 | true | true | 60 | 0.2864
Pipe-132017 | Junction-129775 | Junction-95020 | 34.63 | 0.191 | 43.1 | true | true | 172 | 0.821
Pipe-132023 | Junction-128250 | Junction-127650 | 71.9 | 0.18 | 54.5 | true | true | 321 | 1.5322
Pipe-132491 | Junction-128160 | Junction-127409 | 1.62 | 0.134 | 28.5 | true | true | 60 | 0.2864
Pipe-132494 | Junction-128164 | Junction-128162 | 3.48 | 0.134 | 28.5 | true | true | 60 | 0.2864
Pipe-132496 | Junction-128164 | Junction-127446 | 0.73 | 0.217 | 82.5 | true | true | 962 | 4.5919
Pipe-132497 | Junction-128160 | Junction-128164 | 0.89 | 0.217 | 82.5 | true | true | 962 | 4.5919
Pipe-132516 | Junction-127924 | Junction-128160 | 33.89 | 0.217 | 82.5 | true | true | 962 | 4.5919
Pipe-132556 | Junction-128230 | Junction-128231 | 0.25 | 0.166 | 43.1 | true | true | 172 | 0.821
Pipe-132558 | Junction-128234 | Junction-128233 | 2.71 | 0.166 | 43.1 | true | true | 172 | 0.821
Pipe-132571 | Junction-128246 | Junction-99540 | 0.7 | 0.18 | 54.5 | true | true | 321 | 1.5322
Pipe-132574 | Junction-128234 | Junction-128230 | 0.83 | 0.18 | 54.5 | true | true | 321 | 1.5322
Pipe-132576 | Junction-128250 | Junction-3565 | 0.86 | 0.205 | 70.3 | true | true | 630 | 3.0072
Pipe-132592 | Junction-127382 | Junction-127924 | 56.12 | 0.217 | 82.5 | true | true | 962 | 4.5919
Pipe-132621 | Junction-127268 | Junction-128285 | 0.71 | 0.205 | 70.3 | true | true | 630 | 3.0072
Pipe-132622 | Junction-127268 | Junction-128286 | 0.74 | 0.205 | 70.3 | true | true | 630 | 3.0072
Pipe-132625 | Junction-127286 | Junction-127268 | 34.42 | 0.205 | 70.3 | true | true | 630 | 3.0072
Pipe-132673 | Junction-127208 | Junction-128333 | 2.9 | 0.18 | 54.5 | true | true | 321 | 1.5322
Pipe-132674 | Junction-127208 | Junction-128334 | 1.52 | 0.18 | 54.5 | true | true | 321 | 1.5322
Pipe-132770 | Junction-128432 | Junction-128433 | 7.73 | 0.134 | 28.5 | true | true | 60 | 0.2864
Pipe-132776 | Junction-128439 | Junction-128440 | 7.8 | 0.166 | 43.1 | true | true | 172 | 0.821
Pipe-132930 | Junction-128816 | Junction-128595 | 30.12 | 0.18 | 54.5 | true | true | 321 | 1.5322
Pipe-132952 | Junction-128637 | Junction-128600 | 36.18 | 0.18 | 54.5 | true | true | 321 | 1.5322
Pipe-133222 | Junction-128917 | Junction-127510 | 138.41 | 0.205 | 70.3 | true | true | 630 | 3.0072
Pipe-133347 | Junction-100368 | Junction-129103 | 346.84 | 0.254 | 132.5 | true | true | 3354 | 16.0095
Pipe-133423 | Junction-129145 | Junction-129097 | 1.08 | 0.633 | 54.5 | true | true | 321 | 1.5322
Pipe-133428 | Junction-129103 | Junction-129248 | 16.2 | 0.254 | 132.5 | true | true | 3354 | 16.0095
Pipe-133431 | Junction-129106 | Junction-129107 | 0.64 | 0.614 | 43.1 | true | true | 172 | 0.821
Pipe-133434 | Junction-129111 | Junction-129109 | 4.4 | 0.614 | 43.1 | true | true | 172 | 0.821
Pipe-133436 | Junction-129111 | Junction-129106 | 0.76 | 0.633 | 54.5 | true | true | 321 | 1.5322
Pipe-133437 | Junction-129113 | Junction-129111 | 0.93 | 0.633 | 54.5 | true | true | 321 | 1.5322
Pipe-133456 | Junction-129143 | Junction-129113 | 21.34 | 0.18 | 54.5 | true | true | 321 | 1.5322
Pipe-133470 | Junction-129148 | Junction-129149 | 0.64 | 0.614 | 43.1 | true | true | 172 | 0.821
Pipe-133485 | Junction-129145 | Junction-129148 | 0.61 | 0.661 | 70.3 | true | true | 630 | 3.0072
Pipe-133486 | Junction-129171 | Junction-129145 | 0.89 | 0.661 | 70.3 | true | true | 630 | 3.0072
Pipe-133494 | Junction-129191 | Junction-129171 | 73.78 | 0.205 | 70.3 | true | true | 630 | 3.0072
Pipe-133531 | Junction-129247 | Junction-129285 | 149.87 | 0.18 | 54.5 | true | true | 321 | 1.5322
Pipe-133562 | Junction-129247 | Junction-50543 | 7.9 | 0.303 | 107.1 | true | true | 1915 | 9.1408
Pipe-133563 | Junction-129248 | Junction-129043 | 0.44 | 0.217 | 82.5 | true | true | 962 | 4.5919
Pipe-133564 | Junction-129103 | Junction-129250 | 6.67 | 0.254 | 132.5 | true | true | 3354 | 16.0095
Pipe-133572 | Junction-129097 | Junction-129256 | 0.51 | 0.614 | 43.1 | true | true | 172 | 0.821
Pipe-133591 | Junction-129282 | Junction-129272 | 20.99 | 0.18 | 54.5 | true | true | 321 | 1.5322
Pipe-134497 | Junction-300 | Junction-998 | 158.46 | 0.18 | 54.5 | true | true | 321 | 1.5322
Pipe-134525 | Junction-2359 | Junction-127534 | 6.35 | 0.501 | 210.1 | true | true | 11253 | 53.7136
Pipe-134620 | Junction-127234 | Junction-3534 | 91.23 | 0.205 | 70.3 | true | true | 630 | 3.0072
Pipe-134634 | Junction-128432 | Junction-3421 | 33.66 | 0.18 | 54.5 | true | true | 321 | 1.5322
Pipe-134638 | Junction-3534 | Junction-128432 | 60.15 | 0.18 | 54.5 | true | true | 321 | 1.5322
Pipe-134648 | Junction-129282 | Junction-128250 | 75 | 0.205 | 70.3 | true | true | 630 | 3.0072
Pipe-134654 | Junction-3968 | Junction-127234 | 55.7 | 0.205 | 70.3 | true | true | 630 | 3.0072
Pipe-134658 | Junction-3673 | Junction-129282 | 27.1 | 0.205 | 70.3 | true | true | 630 | 3.0072
Pipe-134826 | Junction-127219 | Junction-129143 | 251.98 | 0.217 | 82.5 | true | true | 962 | 4.5919
Pipe-134839 | Junction-111223 | Junction-127219 | 77.59 | 0.217 | 82.5 | true | true | 962 | 4.5919
Pipe-134865 | Junction-129143 | Junction-8165 | 126.11 | 0.217 | 82.5 | true | true | 962 | 4.5919
Pipe-134938 | Junction-19908 | Junction-128439 | 2.93 | 0.411 | 312.7 | true | true | 31872 | 152.1337
Pipe-134974 | Junction-127514 | Junction-30414 | 35.88 | 0.293 | 210.1 | true | true | 11253 | 53.7136
Pipe-134990 | Junction-28458 | Junction-51072 | 27.2 | 0.225 | 107.1 | true | true | 1915 | 9.1408
Pipe-135079 | Junction-128917 | Junction-126962 | 315.33 | 0.404 | 393.8 | true | true | 58221 | 277.9045
Pipe-135091 | Junction-128439 | Junction-41442 | 152.53 | 0.411 | 312.7 | true | true | 31872 | 152.1337
Pipe-135113 | Junction-51524 | Junction-51072 | 57.23 | 0.225 | 107.1 | true | true | 1915 | 9.1408
Pipe-135153 | Junction-126962 | Junction-20377 | 287.33 | 0.404 | 393.8 | true | true | 58221 | 277.9045
Pipe-135175 | Junction-65528 | Junction-127171 | 75.05 | 0.259 | 82.5 | true | true | 962 | 4.5919
Pipe-135227 | Junction-94950 | Junction-96958 | 109.3 | 0.303 | 107.1 | true | true | 1915 | 9.1408
Pipe-135253 | Junction-71596 | Junction-73054 | 100.71 | 0.217 | 82.5 | true | true | 962 | 4.5919
Pipe-135347 | Junction-97159 | Junction-129247 | 158.93 | 0.303 | 107.1 | true | true | 1915 | 9.1408
Pipe-135385 | Junction-41132 | Junction-64781 | 210.04 | 0.303 | 107.1 | true | true | 1915 | 9.1408
Pipe-135408 | Junction-127184 | Junction-94894 | 43.11 | 0.213 | 54.5 | true | true | 321 | 1.5322
Pipe-135414 | Junction-127197 | Junction-127314 | 95.31 | 0.259 | 82.5 | true | true | 962 | 4.5919
Pipe-135492 | Junction-97159 | Junction-97160 | 9.55 | 1 | 100 | true | true | 1915 | 9.1408
Pipe-135500 | Junction-95634 | Junction-129775 | 87.61 | 0.303 | 107.1 | true | true | 1915 | 9.1408
Pipe-135553 | Junction-72630 | Junction-97918 | 30.02 | 0.213 | 54.5 | true | true | 321 | 1.5322
Pipe-135573 | Junction-98040 | Junction-127385 | 31.98 | 0.254 | 132.5 | true | true | 3354 | 16.0095
Pipe-135588 | Junction-127314 | Junction-96962 | 40.6 | 0.259 | 82.5 | true | true | 962 | 4.5919
Pipe-135590 | Junction-96900 | Junction-127174 | 43.73 | 0.191 | 43.1 | true | true | 172 | 0.821
Pipe-135605 | Junction-99540 | Junction-131108 | 1.88 | 0.18 | 54.5 | true | true | 321 | 1.5322
Pipe-135606 | Junction-128247 | Junction-99544 | 11.6 | 1 | 100 | true | true | 1915 | 9.1408
Pipe-135626 | Junction-127160 | Junction-99013 | 15.45 | 0.191 | 43.1 | true | true | 172 | 0.821
Pipe-135639 | Junction-127286 | Junction-130756 | 14.54 | 0.259 | 82.5 | true | true | 962 | 4.5919
Pipe-135643 | Junction-98465 | Junction-116837 | 15.58 | 0.213 | 54.5 | true | true | 321 | 1.5322
Pipe-135646 | Junction-127265 | Junction-98465 | 33.93 | 0.248 | 70.3 | true | true | 630 | 3.0072
Pipe-135649 | Junction-66675 | Junction-127265 | 54.3 | 0.248 | 70.3 | true | true | 630 | 3.0072
Pipe-135651 | Junction-66675 | Junction-127286 | 71.47 | 0.259 | 82.5 | true | true | 962 | 4.5919
Pipe-135674 | Junction-129043 | Junction-98729 | 64.85 | 0.259 | 82.5 | true | true | 962 | 4.5919
Pipe-135690 | Junction-128247 | Junction-100271 | 6.92 | 1 | 100 | true | true | 1915 | 9.1408
Pipe-135691 | Junction-127538 | Junction-128247 | 0.55 | 1 | 100 | true | true | 1915 | 9.1408
Pipe-135692 | Junction-100272 | Junction-128246 | 19.34 | 0.18 | 54.5 | true | true | 321 | 1.5322
Pipe-135703 | Junction-130756 | Junction-129191 | 142.68 | 0.436 | 160.3 | true | true | 5533 | 26.4105
Pipe-135716 | Junction-127406 | Junction-2140 | 91.1 | 0.364 | 132.5 | true | true | 3354 | 16.0095
Pipe-135774 | Junction-128637 | Junction-103003 | 62.68 | 0.205 | 70.3 | true | true | 630 | 3.0072
Pipe-135810 | Junction-128816 | Junction-128637 | 34.12 | 0.205 | 70.3 | true | true | 630 | 3.0072
Pipe-135821 | Junction-103313 | Junction-128816 | 109.01 | 0.205 | 70.3 | true | true | 630 | 3.0072
Pipe-136112 | Junction-127533 | Junction-2039 | 360.36 | 0.355 | 263 | true | true | 20264 | 96.7255
Pipe-136113 | Junction-129191 | Junction-98224 | 126.86 | 0.436 | 160.3 | true | true | 5533 | 26.4105
Pipe-136114 | Junction-98465 | Junction-98461 | 54.91 | 0.248 | 70.3 | true | true | 630 | 3.0072
Pipe-136115 | Junction-129775 | Junction-94950 | 165.28 | 0.303 | 107.1 | true | true | 1915 | 9.1408
Pipe-136122 | Junction-127332 | Junction-111225 | 80.55 | 0.404 | 393.8 | true | true | 58221 | 277.9045

## Node Types
Name | X-Coordinate | Y-Coordinate | Z-Coordinate (Elevation) | Node Type
Sarfvik | 366746.8198 | 6670874.7515 | 20.5968 | Source/Heater
Kirkkonummi | 357050.9258 | 6667510.8984 | 6.2222 | Source/Heater
Ericsson | 361886.5987 | 6668476.9389 | 14.086 | Source/Heater
Hommaksenkaari_EMP | 362957.4922 | 6672797.7812 | 22.9533 | Sink/User
Junction-165 | 364401.5156 | 6671500.4922 | 6.7584 | Junction
Junction-192 | 364377.5 | 6671497.0156 | 5.8102 | Sink/User
Junction-300 | 358080.9961 | 6668891.418 | 16.4505 | Junction
Junction-736 | 357586.0703 | 6667735.5625 | 7.7972 | Sink/User
Junction-894 | 363188.4648 | 6671720.3203 | 15.4241 | Sink/User
Junction-897 | 363184.2344 | 6671714.7383 | 15.429 | Junction
Junction-907 | 363070.9961 | 6671486.7227 | 21.3556 | Junction
Junction-909 | 363087.668 | 6671515.0195 | 22.1726 | Junction
Junction-916 | 363094.8047 | 6671511.3516 | 21.7141 | Junction
Junction-917 | 363157.7031 | 6671580.2109 | 15.9985 | Junction
Junction-919 | 363156.8984 | 6671579.3203 | 16.0729 | Junction
Junction-920 | 363157.1758 | 6671579.5977 | 16.0471 | Junction
Junction-942 | 359799.1953 | 6667611.9023 | 11.5752 | Junction
Junction-945 | 357977.0508 | 6669012.2344 | 18.6289 | Sink/User
Junction-954 | 357975.0117 | 6668977.4805 | 19.2134 | Junction
Junction-956 | 357925.0312 | 6669006.9609 | 18.6796 | Sink/User
Junction-998 | 357973.7461 | 6668973.6836 | 19.1534 | Junction
Junction-1036 | 363071.7266 | 6671487.5234 | 21.3796 | Junction
Junction-1044 | 363086.8555 | 6671469.4375 | 20.5044 | Junction
Junction-1114 | 363060.6914 | 6671435.6016 | 19.6102 | Sink/User
Junction-1124 | 356014.8555 | 6663694.6836 | 9.1376 | Sink/User
Junction-1143 | 356030.5859 | 6663710.3945 | 6.5839 | Junction
Junction-1164 | 359775.7617 | 6667641.3945 | 15.0349 | Sink/User
Junction-1395 | 357605.4805 | 6667699.9258 | 7.7167 | Junction
Junction-1396 | 357637.5469 | 6667718.3242 | 7.8781 | Junction
Junction-1398 | 363121.0391 | 6671387.75 | 15.3552 | Sink/User
Junction-1455 | 357024.2734 | 6667760.2656 | 9.2679 | Junction
Junction-1457 | 357046.3125 | 6667749.7969 | 8.9751 | Junction
Junction-1459 | 357045.0312 | 6667749.8398 | 8.9622 | Junction
Junction-1461 | 357045.4414 | 6667747.2461 | 8.8595 | Junction
Junction-1470 | 357018.0742 | 6667761.5938 | 9.3178 | Junction
Junction-1471 | 357018.5469 | 6667762.9961 | 9.3759 | Junction
Junction-1472 | 357017.9023 | 6667761.2031 | 9.3017 | Junction
Junction-1473 | 357015.1172 | 6667754.9531 | 9.0549 | Sink/User
Junction-1475 | 356983.8711 | 6667780.4453 | 10.0947 | Junction
Junction-1477 | 356973.6094 | 6667774.0156 | 9.9371 | Sink/User
Junction-1489 | 356985.4531 | 6667779.0312 | 10.0428 | Junction
Junction-1491 | 356982.6445 | 6667762.4922 | 9.4798 | Sink/User
Junction-1501 | 356987.8125 | 6667778.0078 | 9.9991 | Junction
Junction-1503 | 356989.0469 | 6667784.1523 | 10.1988 | Junction
Junction-1510 | 356986.8281 | 6667778.457 | 10.0182 | Junction
Junction-1512 | 356989.7812 | 6667789.6328 | 10.3751 | Junction
Junction-1513 | 357044.4883 | 6667744.0625 | 8.7176 | Junction
Junction-1694 | 362900.8555 | 6671311.8789 | 13.2348 | Sink/User
Junction-1704 | 362928.6836 | 6671288.625 | 13.703 | Junction
Junction-1917 | 356012.8086 | 6663568.4102 | 16.0624 | Sink/User
Junction-1928 | 356029.293 | 6663555.0664 | 17.223 | Junction
Junction-1933 | 363167.8242 | 6671366.3359 | 15.4203 | Sink/User
Junction-1941 | 357049.1133 | 6667773.0312 | 9.9873 | Sink/User
Junction-2006 | 358017.0703 | 6668703.4922 | 16.4788 | Junction
Junction-2007 | 358017.0898 | 6668703.4883 | 16.4774 | Junction
Junction-2009 | 358018.1211 | 6668703.2852 | 16.406 | Junction
Junction-2039 | 357052.1367 | 6667519.3125 | 6.4127 | Junction
Junction-2040 | 357051.4336 | 6667514.543 | 6.3049 | Junction
Junction-2042 | 357112.7266 | 6667950.0703 | 18.0564 | Junction
Junction-2091 | 357986.4883 | 6668585.9258 | 25.9274 | Junction
Junction-2097 | 357970.2344 | 6668558.9297 | 25.9907 | Junction
Junction-2098 | 357968.8555 | 6668559.7617 | 26.0715 | Junction
Junction-2100 | 357965.332 | 6668553.5508 | 25.9541 | Junction
Junction-2103 | 357963.9023 | 6668554.3906 | 26.04 | Junction
Junction-2140 | 357084.0703 | 6667942.9141 | 18.7282 | Junction
Junction-2147 | 357079.1016 | 6667963.2812 | 19.2217 | Junction
Junction-2150 | 357458.7109 | 6667634.3594 | 6.8396 | Junction
Junction-2160 | 357462.2461 | 6667633.6797 | 6.8691 | Junction
Junction-2226 | 357820.3047 | 6668420.8398 | 26.8356 | Junction
Junction-2227 | 357820.2969 | 6668420.7266 | 26.8275 | Junction
Junction-2228 | 357826.9961 | 6668443.5352 | 28.4221 | Junction
Junction-2237 | 357820.1836 | 6668421.2227 | 26.8624 | Junction
Junction-2238 | 357820.3359 | 6668421.2461 | 26.8648 | Junction
Junction-2251 | 357547.9648 | 6667666.8672 | 7.288 | Junction
Junction-2330 | 357129.9102 | 6667903.9883 | 16.5853 | Sink/User
Junction-2340 | 357128.0625 | 6667893.1328 | 15.9806 | Junction
Junction-2359 | 357334.6367 | 6667597.4531 | 6.4885 | Junction
Junction-2360 | 357550.6875 | 6667668.4922 | 7.2914 | Junction
Junction-2365 | 359860.8555 | 6667602.5352 | 12.809 | Sink/User
Junction-2961 | 355901.6641 | 6663856.2656 | 11.1591 | Junction
Junction-2964 | 355900.5156 | 6663855.9219 | 11.1698 | Junction
Junction-3165 | 362734.582 | 6671527.168 | 15.3587 | Junction
Junction-3224 | 362740.0195 | 6671592.5898 | 17.5862 | Junction
Junction-3306 | 357020.8555 | 6667491.0195 | 5.4434 | Junction
Junction-3397 | 359809.0156 | 6667545.2734 | 9.3904 | Sink/User
Junction-3421 | 363156.4492 | 6672037.4062 | 17.6991 | Junction
Junction-3489 | 359778.9883 | 6667556.0586 | 10.6632 | Junction
Junction-3493 | 355737.9062 | 6663623.832 | 14.1105 | Sink/User
Junction-3534 | 363146.1719 | 6671951.7305 | 17.3915 | Junction
Junction-3552 | 363162.3633 | 6671907.9023 | 15.7836 | Junction
Junction-3565 | 363238.6328 | 6671858.8516 | 14.3949 | Junction
Junction-3673 | 363325.2383 | 6671806.6992 | 14.3971 | Junction
Junction-3911 | 355780.4805 | 6663592.1133 | 14.7526 | Junction
Junction-3968 | 363290.2656 | 6671943.6641 | 12.8128 | Junction
Junction-4076 | 363370.5195 | 6671911.2617 | 14.3987 | Junction
Junction-4079 | 362863.0352 | 6671228.3711 | 14.2535 | Sink/User
Junction-4108 | 355094.9414 | 6664546.0234 | 9.0849 | Sink/User
Junction-4122 | 355132.2891 | 6664517.4883 | 7.4663 | Junction
Junction-4364 | 362888.9062 | 6671209.2227 | 14.2311 | Junction
Junction-4719 | 356076.2734 | 6664766.8672 | 10.0754 | Junction
Junction-4720 | 356077.0742 | 6664768.7148 | 10.1291 | Junction
Junction-4721 | 356077.6602 | 6664770.0078 | 10.1668 | Junction
Junction-5284 | 355928.4883 | 6663816.0703 | 10.0023 | Junction
Junction-5297 | 355922.6445 | 6663861.6289 | 11.1112 | Junction
Junction-5699 | 364077.8438 | 6671349.3047 | 6.4767 | Sink/User
Junction-5882 | 357040.2695 | 6667346.457 | 9.066 | Sink/User
Junction-6013 | 364018.0156 | 6671421.3828 | 6.7924 | Junction
Junction-6217 | 357019.2109 | 6667327.2344 | 10.6257 | Junction
Junction-6487 | 360373.6406 | 6668572.1875 | 16.7232 | Junction
Junction-6583 | 363035.8906 | 6671230.8125 | 12.7321 | Sink/User
Junction-6592 | 356793.5625 | 6668123.4648 | 23.5313 | Junction
Junction-6630 | 366494.8555 | 6670618.3828 | 22.0711 | Junction
Junction-6643 | 363035.9492 | 6671250.6094 | 12.9753 | Junction
Junction-6657 | 355175.4922 | 6664602.5664 | 10.4475 | Sink/User
Junction-6710 | 356793.4688 | 6668106.7891 | 22.2818 | Junction
Junction-6712 | 356791.7227 | 6668132.7539 | 24.2018 | Sink/User
Junction-6716 | 359867.7734 | 6667677.6094 | 15.2974 | Sink/User
Junction-6737 | 366474.5977 | 6670657.8867 | 22.3916 | Junction
Junction-6834 | 359870.8438 | 6667639.3633 | 13.5419 | Junction
Junction-6835 | 359873.6289 | 6667639.8672 | 13.6051 | Junction
Junction-7028 | 355174.0898 | 6664589.1094 | 10.3652 | Junction
Junction-7055 | 355149.168 | 6664518.2539 | 7.7397 | Junction
Junction-7150 | 359557.8516 | 6667438.0117 | 9.8486 | Sink/User
Junction-7161 | 359546.9219 | 6667434.3672 | 9.6744 | Junction
Junction-7222 | 360352.3164 | 6668611.2227 | 16.4694 | Junction
Junction-7270 | 359528.6484 | 6667407.4805 | 9.098 | Sink/User
Junction-7285 | 359553.5898 | 6667424.4336 | 9.3494 | Junction
Junction-7434 | 364302.0586 | 6671703.4219 | 6.3071 | Junction
Junction-7442 | 364320.0781 | 6671712.25 | 6.9487 | Junction
Junction-7443 | 364308.5039 | 6671706.5312 | 6.5504 | Junction
Junction-7518 | 355436.1758 | 6664594.7109 | 9.0058 | Junction
Junction-7612 | 359554.3984 | 6667423.1992 | 9.3067 | Junction
Junction-7613 | 360569.4844 | 6668536.5703 | 22.6512 | Junction
Junction-7614 | 360567.5273 | 6668536.9219 | 22.8919 | Sink/User
Junction-7795 | 362327.3242 | 6669055.1797 | 9.0833 | Junction
Junction-7838 | 366585.7734 | 6670632.1641 | 31.6498 | Sink/User
Junction-7879 | 361988.6445 | 6668520.2617 | 15.483 | Junction
Junction-7883 | 361996.5078 | 6668525.3555 | 15.584 | Junction
Junction-8112 | 356889.3789 | 6668033.9023 | 17.976 | Junction
Junction-8150 | 364561.8164 | 6671548.207 | 10.7783 | Sink/User
Junction-8165 | 364569.2422 | 6671551.8086 | 10.9154 | Junction
Junction-9041 | 363200.7422 | 6671235.625 | 12.8759 | Junction
Junction-9062 | 363237.1875 | 6671675.5391 | 13.0109 | Junction
Junction-9115 | 363214.168 | 6671253.7773 | 13.0812 | Junction
Junction-9137 | 363236.2031 | 6671285.5508 | 12.6305 | Junction
Junction-9252 | 357643.0977 | 6668193.1914 | 12.899 | Junction
Junction-9492 | 357646.6641 | 6668166.5547 | 12.9035 | Junction
Junction-9494 | 357258.8086 | 6667888.8125 | 25.2763 | Sink/User
Junction-9548 | 358046.9258 | 6668858.3594 | 17.5978 | Junction
Junction-9551 | 357209.1406 | 6667851.4336 | 24.6911 | Junction
Junction-9556 | 357237.1523 | 6667501.6914 | 6.8723 | Junction
Junction-9698 | 357645.4258 | 6668134.5977 | 13.023 | Sink/User
Junction-9802 | 357643.6875 | 6668134.5742 | 13.0346 | Junction
Junction-9808 | 358186.5625 | 6668584.6289 | 11.8709 | Junction
Junction-9809 | 358187.0938 | 6668585.4688 | 11.9007 | Junction
Junction-9860 | 358299.6211 | 6667761.375 | 29.7141 | Sink/User
Junction-9915 | 357288.3125 | 6667486.4961 | 6.6789 | Junction
Junction-9917 | 357295.1016 | 6667484.5039 | 6.7273 | Junction
Junction-9944 | 358365.5117 | 6667775.2188 | 29.1357 | Junction
Junction-9946 | 358263.3984 | 6667549.332 | 29.6155 | Sink/User
Junction-9981 | 358088.793 | 6668463.4023 | 13.6311 | Junction
Junction-9986 | 358210.8477 | 6668807.1641 | 13.4601 | Junction
Junction-10018 | 357335.6992 | 6667689.9453 | 7.5496 | Junction
Junction-10094 | 363779.8945 | 6671140.793 | 8.3218 | Junction
Junction-10095 | 363781.0977 | 6671142.6211 | 8.3393 | Sink/User
Junction-10097 | 363777.5742 | 6671141.4219 | 8.3841 | Junction
Junction-10099 | 363776.1289 | 6671143.0352 | 8.4559 | Sink/User
Junction-10100 | 363777.2148 | 6671140.8867 | 8.3779 | Junction
Junction-10202 | 357366.9336 | 6668577.7578 | 22.7121 | Junction
Junction-10258 | 363202.7852 | 6671336.8359 | 15.6396 | Sink/User
Junction-10260 | 363192.5352 | 6671323.4492 | 15.0735 | Junction
Junction-10392 | 358192.0156 | 6668596.3906 | 12.315 | Junction
Junction-10519 | 357447.3945 | 6668606.2773 | 25.2517 | Junction
Junction-10595 | 358016.5273 | 6668848.1016 | 17.5049 | Sink/User
Junction-10823 | 358422.3906 | 6667708.1406 | 23.7784 | Junction
Junction-11218 | 358675.7734 | 6667794.4141 | 29.9422 | Junction
Junction-11221 | 357338.0977 | 6668615.9062 | 24.8683 | Sink/User
Junction-11647 | 358384.6562 | 6667665.7656 | 22.1959 | Junction
Junction-11651 | 358355.1797 | 6667642.4961 | 23.8039 | Sink/User
Junction-12744 | 357293.7617 | 6667479.7617 | 6.6598 | Sink/User
Junction-12748 | 357333.3398 | 6667473.2031 | 7.0232 | Junction
Junction-13700 | 359711.9922 | 6667764.2539 | 17.7158 | Junction
Junction-13715 | 359643.1797 | 6668078.8828 | 18.6338 | Junction
Junction-13742 | 357150.5742 | 6665651.6289 | 14.8366 | Junction
Junction-13761 | 357073.6289 | 6665609.5859 | 12.4267 | Junction
Junction-14261 | 365343.5781 | 6670121.3477 | 29.5078 | Junction
Junction-14279 | 361849.0898 | 6669065.418 | 2.2032 | Junction
Junction-14292 | 361556.3125 | 6668899.5352 | 4.5682 | Junction
Junction-14297 | 361456.6641 | 6668889.3086 | 2.5479 | Junction
Junction-15021 | 355987.9336 | 6663853.5156 | 10.1492 | Sink/User
Junction-15027 | 357135.8164 | 6665676.6992 | 20.4855 | Sink/User
Junction-15412 | 357967.5352 | 6668557.9531 | 26.05 | Junction
Junction-15414 | 357968.5664 | 6668557.0586 | 25.976 | Junction
Junction-15720 | 359314.3594 | 6668405.3359 | 29.9767 | Junction
Junction-16187 | 357016.7891 | 6668781.0664 | 20.6369 | Sink/User
Junction-16220 | 355981.1055 | 6663871.2734 | 11.4639 | Junction
Junction-16232 | 355992.3398 | 6663870.8008 | 11.1809 | Junction
Junction-16278 | 357011.9453 | 6668786.7539 | 20.5871 | Junction
Junction-16338 | 359503.2148 | 6668190.3867 | 25.5136 | Junction
Junction-16340 | 359517.3984 | 6668163.7852 | 22.6638 | Junction
Junction-16557 | 359283.2461 | 6668394.3398 | 29.4467 | Sink/User
Junction-16565 | 366039.9648 | 6670163.3906 | 26.2032 | Junction
Junction-16605 | 359531.3945 | 6667403.9336 | 8.9601 | Sink/User
Junction-16793 | 363301.3984 | 6672539.9297 | 19.0555 | Sink/User
Junction-16837 | 357827.5039 | 6667826.8359 | 8.3545 | Sink/User
Junction-17058 | 363279.7578 | 6672527.4023 | 20.7838 | Junction
Junction-17125 | 358191.3242 | 6666317.5156 | 11.8415 | Junction
Junction-17137 | 363009.8555 | 6671314.4336 | 16.1424 | Sink/User
Junction-17173 | 357790.082 | 6667785.4922 | 8.4455 | Junction
Junction-17277 | 357915.25 | 6668506.0039 | 28.622 | Junction
Junction-17278 | 357916.4414 | 6668505.4531 | 28.4203 | Junction
Junction-17342 | 358016.9297 | 6668703.5195 | 16.4884 | Junction
Junction-17528 | 357326.1016 | 6667475.1719 | 6.967 | Junction
Junction-17656 | 366162.6133 | 6670112.8281 | 24.3294 | Junction
Junction-17746 | 366066.2031 | 6670153.4531 | 25.5601 | Junction
Junction-18008 | 357915.3906 | 6668505.9453 | 28.5987 | Junction
Junction-18013 | 357965.4609 | 6668552.9766 | 25.9262 | Junction
Junction-18016 | 358012.6797 | 6668520.6875 | 21.9784 | Junction
Junction-18017 | 357968.7148 | 6668560.3398 | 26.0981 | Junction
Junction-18021 | 357984.9102 | 6668586.707 | 26.0234 | Junction
Junction-18024 | 357986.1562 | 6668585.918 | 25.9486 | Junction
Junction-18027 | 358017.1367 | 6668703.7852 | 16.4652 | Junction
Junction-18033 | 357967.4062 | 6668558.0312 | 26.0579 | Junction
Junction-18065 | 358085.5898 | 6668463.9062 | 13.7438 | Junction
Junction-18841 | 357828.4453 | 6668442.625 | 28.327 | Junction
Junction-18843 | 357829.1836 | 6668442.5781 | 28.3105 | Junction
Junction-18873 | 355438.0742 | 6664596.0234 | 8.9182 | Junction
Junction-18874 | 355411.6172 | 6664621.4258 | 10.1282 | Sink/User
Junction-18899 | 358295.3984 | 6669181.3164 | 22.7351 | Junction
Junction-18900 | 358292.2344 | 6669173.8867 | 21.8799 | Junction
Junction-18913 | 357131.0195 | 6667891.6523 | 15.9788 | Junction
Junction-18916 | 357128.9805 | 6667890.7617 | 15.8638 | Junction
Junction-19185 | 357188.1562 | 6667929.4102 | 17.5499 | Sink/User
Junction-19191 | 357192.4336 | 6667923.168 | 17.6014 | Junction
Junction-19192 | 357202.3242 | 6667928.7578 | 17.7655 | Junction
Junction-19194 | 357181.1797 | 6667909.5078 | 17.3863 | Junction
Junction-19266 | 358084.3906 | 6668270.0703 | 10.0473 | Sink/User
Junction-19267 | 358081.1367 | 6668273.4297 | 10.1406 | Junction
Junction-19268 | 358112.5859 | 6668300.2578 | 9.6094 | Junction
Junction-19274 | 358141.418 | 6668440.3789 | 11.8849 | Sink/User
Junction-19572 | 358340.7695 | 6669338.5898 | 31.8059 | Sink/User
Junction-19573 | 358357.3984 | 6669327.0977 | 28.4954 | Junction
Junction-19575 | 358357.125 | 6669326.4844 | 28.4811 | Junction
Junction-19576 | 358336.5312 | 6669278.0195 | 26.4054 | Junction
Junction-19606 | 358368.418 | 6669373.793 | 30.8388 | Junction
Junction-19608 | 358358.9727 | 6669330.625 | 28.5668 | Junction
Junction-19611 | 358316.6367 | 6669285.7422 | 27.7935 | Sink/User
Junction-19612 | 358337.25 | 6669279.7305 | 26.4357 | Junction
Junction-19616 | 358251.5234 | 6669155.1719 | 22.8219 | Sink/User
Junction-19621 | 358190.4961 | 6669099.8555 | 20.3992 | Sink/User
Junction-19666 | 359553.3672 | 6667424.7734 | 9.361 | Junction
Junction-19699 | 359531.9766 | 6667446.3711 | 9.9429 | Junction
Junction-19701 | 359541.0781 | 6667454.4531 | 10.115 | Junction
Junction-19740 | 362977.8477 | 6671251.7148 | 14.0673 | Sink/User
Junction-19908 | 363653.9375 | 6671072.7539 | 11.4418 | Junction
Junction-19911 | 363633.3711 | 6671123.9453 | 11.2888 | Sink/User
Junction-19916 | 363630.6758 | 6671121.707 | 11.6024 | Junction
Junction-20194 | 357950.3633 | 6668577.6641 | 27.8139 | Sink/User
Junction-20195 | 357949.9922 | 6668576.7305 | 27.7881 | Junction
Junction-20196 | 357949.7109 | 6668577.1523 | 27.8256 | Sink/User
Junction-20230 | 358426.7891 | 6669285.8438 | 23.3153 | Junction
Junction-20232 | 358489.8359 | 6669276.3906 | 20.2084 | Sink/User
Junction-20234 | 358485.4375 | 6669263.8398 | 20.9308 | Junction
Junction-20236 | 358483.543 | 6669254.3672 | 21.4737 | Sink/User
Junction-20237 | 358508.6523 | 6669385.1211 | 23.3353 | Junction
Junction-20238 | 358520.9609 | 6669379.793 | 21.2825 | Sink/User
Junction-20284 | 363085.0234 | 6671267.4336 | 13.6152 | Sink/User
Junction-20306 | 359574.0312 | 6667484.0312 | 12.0237 | Junction
Junction-20377 | 365821.6523 | 6670267.8008 | 30.4003 | Junction
Junction-20653 | 358548.8086 | 6669499.0078 | 25.7604 | Sink/User
Junction-20655 | 358424.125 | 6669287.0312 | 23.3633 | Junction
Junction-20656 | 358537.4375 | 6669452.4727 | 22.8981 | Junction
Junction-20659 | 358539.625 | 6669457.4648 | 23.0677 | Junction
Junction-20661 | 358584.2461 | 6669438.7969 | 21.0254 | Sink/User
Junction-20663 | 358407.0078 | 6669357.8594 | 29.5443 | Junction
Junction-20664 | 358406.2305 | 6669358.1797 | 29.5525 | Junction
Junction-20691 | 358257.7305 | 6669110.7344 | 18.4978 | Junction
Junction-20761 | 359470.2461 | 6667406.625 | 11.8052 | Junction
Junction-20819 | 359578.2188 | 6667492.3984 | 13.1482 | Junction
Junction-21263 | 357782.3945 | 6666405.7969 | 27.8955 | Junction
Junction-21264 | 357787.9336 | 6666428.4688 | 27.687 | Junction
Junction-21265 | 357919.5508 | 6667895.1875 | 7.3737 | Junction
Junction-21321 | 363098.9531 | 6671461.082 | 19.7957 | Junction
Junction-21414 | 357010.0859 | 6669232.25 | 39.7644 | Sink/User
Junction-21554 | 358352.0977 | 6669270.9453 | 25.7808 | Junction
Junction-21588 | 363609.8672 | 6671064.7539 | 13.5507 | Sink/User
Junction-21635 | 358405.2031 | 6669234.5977 | 24.072 | Sink/User
Junction-21636 | 358402.5703 | 6669235.7109 | 24.2505 | Junction
Junction-21644 | 359767.1914 | 6667560.4141 | 11.6976 | Junction
Junction-21646 | 360017.3906 | 6667671.5391 | 14.0142 | Junction
Junction-21775 | 359573.375 | 6667398.5859 | 7.5193 | Sink/User
Junction-21783 | 359554.5312 | 6667385.9062 | 7.533 | Junction
Junction-21859 | 358370.2109 | 6669176.9492 | 23.2141 | Sink/User
Junction-21896 | 359896.7227 | 6667644.4062 | 14.1222 | Junction
Junction-22022 | 359623.5078 | 6667427.1758 | 7.5253 | Junction
Junction-22039 | 358407.2695 | 6669357.75 | 29.5413 | Junction
Junction-22041 | 358408.0273 | 6669363.1875 | 30.0832 | Junction
Junction-22045 | 358540.2812 | 6669491.6836 | 25.6448 | Junction
Junction-22175 | 357774.1094 | 6667538.1719 | 8.0372 | Junction
Junction-22540 | 356078.6367 | 6664771.8242 | 10.2089 | Junction
Junction-22905 | 358514.8555 | 6669506.0352 | 26.9915 | Sink/User
Junction-22908 | 363130.7031 | 6671264.1992 | 14.0617 | Sink/User
Junction-22919 | 363099.207 | 6671232.1719 | 13.3463 | Junction
Junction-23009 | 357830.9883 | 6666392.25 | 26.0773 | Sink/User
Junction-23337 | 355525.0859 | 6664665.3008 | 10.6401 | Junction
Junction-23339 | 357197.7695 | 6666266.2188 | 18.1422 | Junction
Junction-23720 | 357882.6523 | 6667890.5352 | 7.733 | Sink/User
Junction-23736 | 361391.0781 | 6669063.7969 | 9.3682 | Sink/User
Junction-24920 | 357848.4844 | 6668408.1445 | 26.0515 | Sink/User
Junction-25321 | 357963.6719 | 6667804.5938 | 5.7383 | Sink/User
Junction-25472 | 358086.6172 | 6667520.9648 | 5.8393 | Sink/User
Junction-25486 | 358062.4453 | 6667524.0312 | 6.8633 | Junction
Junction-25489 | 356977.4219 | 6665881.9102 | 29.5361 | Sink/User
Junction-25543 | 357968.4297 | 6667794.3789 | 5.2428 | Junction
Junction-26246 | 357844.043 | 6668415.2773 | 26.4904 | Junction
Junction-26248 | 357916.3164 | 6667931.9023 | 7.7986 | Junction
Junction-26973 | 363393.3711 | 6672422.625 | 15.8341 | Junction
Junction-26989 | 356908.6133 | 6665869.8125 | 25.08 | Junction
Junction-26996 | 356915.3828 | 6665851.7656 | 24.7907 | Junction
Junction-26998 | 363037.9258 | 6671358.1875 | 16.3535 | Sink/User
Junction-27084 | 357028.9336 | 6665763.0273 | 30.5874 | Junction
Junction-27239 | 357007.293 | 6665737.0508 | 31.4105 | Sink/User
Junction-27498 | 357744.7852 | 6667927.1641 | 7.5045 | Junction
Junction-27501 | 357806.6289 | 6667760.7812 | 8.4364 | Sink/User
Junction-27615 | 363373.1172 | 6672405.9492 | 15.4867 | Sink/User
Junction-28458 | 356984.0195 | 6667279.6328 | 12.3286 | Junction
Junction-28618 | 356989.4766 | 6665855.5 | 29.6143 | Junction
Junction-29012 | 356957.5039 | 6667309.5742 | 13.1695 | Sink/User
Junction-29352 | 356864.4531 | 6667252.6797 | 15.0305 | Junction
Junction-29484 | 358014.3594 | 6668576.0664 | 23.7686 | Sink/User
Junction-29629 | 358052.1367 | 6667519.1914 | 6.8505 | Sink/User
Junction-29632 | 358062.957 | 6667520.5977 | 6.8248 | Junction
Junction-29864 | 356946.4453 | 6665971.2969 | 26.8288 | Sink/User
Junction-29873 | 356972.5586 | 6665986.2578 | 24.4471 | Junction
Junction-29936 | 361650.75 | 6668805.0664 | 1.3443 | Junction
Junction-29939 | 356855.8398 | 6667279.543 | 14.5946 | Sink/User
Junction-29994 | 362987.9102 | 6671057.4219 | 14.3445 | Sink/User
Junction-30008 | 362914.7773 | 6671151.6914 | 16.0987 | Junction
Junction-30414 | 357328.5039 | 6667634.0586 | 6.5899 | Junction
Junction-30575 | 357151.4102 | 6668539.2148 | 24.5315 | Sink/User
Junction-30728 | 357158.1562 | 6668476.3711 | 22.8839 | Junction
Junction-31466 | 363072.4414 | 6671250.2266 | 13.4065 | Junction
Junction-31469 | 363100.7656 | 6671231.1367 | 13.3459 | Junction
Junction-31545 | 363044.2383 | 6671297.8125 | 15.6902 | Junction
Junction-31656 | 363167.5898 | 6671189.8672 | 12.1087 | Junction
Junction-31657 | 363248.8594 | 6672218.1641 | 18.5325 | Junction
Junction-31788 | 363046.7383 | 6671279.4297 | 15.0192 | Junction
Junction-31915 | 365136.0977 | 6670400.3281 | 27.6504 | Junction
Junction-31937 | 358073.3242 | 6667558.8008 | 5.1517 | Sink/User
Junction-31990 | 358056.9766 | 6667560.2383 | 6.5615 | Junction
Junction-32090 | 359531.4375 | 6667468.418 | 10.1896 | Sink/User
Junction-32340 | 363146.6367 | 6671158.4414 | 11.9851 | Junction
Junction-32341 | 363138.2148 | 6671145.3672 | 9.3119 | Junction
Junction-32344 | 363097.5352 | 6671214.8945 | 13.0914 | Sink/User
Junction-32353 | 363162.0742 | 6671325.3477 | 14.8658 | Junction
Junction-32355 | 363186.3359 | 6671312.9453 | 14.7027 | Junction
Junction-32358 | 363076.3086 | 6671354.7578 | 15.7374 | Junction
Junction-32382 | 363062.957 | 6671258.2383 | 13.5636 | Junction
Junction-32586 | 363058.8555 | 6671366.2891 | 16.3005 | Junction
Junction-32591 | 363078.6562 | 6671352.9844 | 15.6552 | Junction
Junction-32703 | 363095.5117 | 6671340.8203 | 15.2327 | Junction
Junction-32957 | 357324.9258 | 6666143.1914 | 33.9091 | Sink/User
Junction-33148 | 365178.4805 | 6670379.1133 | 29.47 | Junction
Junction-33431 | 357420.7383 | 6667442.9375 | 7.0797 | Junction
Junction-33432 | 357401.3008 | 6667447.793 | 7.1272 | Junction
Junction-33839 | 356083.0586 | 6663882.4375 | 11.515 | Sink/User
Junction-33846 | 363191.7031 | 6671563.4375 | 14.857 | Junction
Junction-33847 | 363192.3281 | 6671565.5195 | 14.7858 | Junction
Junction-33920 | 363091.9336 | 6671335.8047 | 15.1913 | Sink/User
Junction-33952 | 356758.6953 | 6667894.3672 | 14.7794 | Sink/User
Junction-33957 | 356755.5742 | 6667930.7773 | 16.5691 | Junction
Junction-34033 | 357941.9258 | 6668125.3594 | 8.4294 | Junction
Junction-34066 | 363231.7656 | 6671533.8281 | 12.6999 | Junction
Junction-34067 | 363198.9609 | 6671572.3828 | 14.427 | Sink/User
Junction-34155 | 357805.5625 | 6666446.8633 | 26.2235 | Sink/User
Junction-34156 | 357792.6445 | 6666448.8516 | 27.1694 | Junction
Junction-34191 | 357722.9141 | 6667714.7969 | 9.7141 | Sink/User
Junction-34248 | 357340.1133 | 6666123.8633 | 35.1267 | Junction
Junction-34250 | 363164.9492 | 6672181.8828 | 20.2917 | Sink/User
Junction-34334 | 357305.6055 | 6666060.293 | 35.6311 | Junction
Junction-34444 | 357844.1406 | 6667486.3633 | 7.7773 | Junction
Junction-34547 | 357719.5312 | 6667712.0117 | 9.8398 | Junction
Junction-35245 | 357295.8633 | 6666070.8984 | 35.9718 | Sink/User
Junction-35697 | 357741.9531 | 6667928.582 | 7.504 | Junction
Junction-35760 | 357948.9609 | 6667707.1875 | 7.2111 | Junction
Junction-35793 | 358035.0195 | 6667610.8008 | 5.1683 | Sink/User
Junction-35794 | 358043.2891 | 6667597.0273 | 5.5174 | Junction
Junction-35871 | 357215.1211 | 6666259.9727 | 20.6134 | Junction
Junction-36016 | 356960.3711 | 6667807.1406 | 10.8261 | Sink/User
Junction-36047 | 357794.1758 | 6667716.8438 | 8.829 | Junction
Junction-36258 | 357781.3867 | 6667783.5273 | 8.4539 | Junction
Junction-36301 | 357773.0586 | 6667544.3789 | 8.0477 | Junction
Junction-36469 | 357282.1641 | 6666264.7109 | 25.7312 | Junction
Junction-36471 | 357217.25 | 6666260.0938 | 20.6082 | Junction
Junction-36476 | 358069.0508 | 6667447.9062 | 6.1854 | Junction
Junction-36767 | 357198.0781 | 6666266.6367 | 18.0904 | Junction
Junction-36773 | 357752.9961 | 6667929.3633 | 7.5399 | Junction
Junction-36951 | 357268.2695 | 6669516.8203 | 43.5247 | Junction
Junction-36958 | 357116.793 | 6669470.4648 | 47.4916 | Junction
Junction-36960 | 357119.4805 | 6669462.3047 | 46.5424 | Sink/User
Junction-36962 | 357061.7656 | 6669457.9102 | 50.6687 | Junction
Junction-36967 | 357043.043 | 6669449.0898 | 52.6532 | Junction
Junction-36968 | 357209.582 | 6669507.8633 | 46.2314 | Junction
Junction-37011 | 356963.793 | 6667816.668 | 11.0963 | Junction
Junction-37299 | 357173.4023 | 6666113.0391 | 28.3942 | Junction
Junction-37303 | 357194.0586 | 6666118.3555 | 29.7515 | Junction
Junction-37316 | 358069.6836 | 6667478.6445 | 5.8086 | Junction
Junction-37396 | 357389.8438 | 6669273.0156 | 25.1653 | Junction
Junction-37544 | 357307.5547 | 6669438.0508 | 32.0592 | Junction
Junction-37550 | 357326.3867 | 6669483.9883 | 35.2578 | Junction
Junction-37591 | 357520.6953 | 6666455.7344 | 37.2845 | Sink/User
Junction-37596 | 357518.4883 | 6666432.9453 | 37.5636 | Junction
Junction-37605 | 357389.5859 | 6669253.8203 | 24.2234 | Junction
Junction-37727 | 362822.2422 | 6672899.4492 | 18.2147 | Junction
Junction-37731 | 362846.7148 | 6672827.1914 | 18.7583 | Junction
Junction-37764 | 357279.5312 | 6669418.9688 | 30.5659 | Junction
Junction-37780 | 357273.2031 | 6669539.4414 | 45.913 | Sink/User
Junction-37782 | 357212.7227 | 6669500.1719 | 44.963 | Sink/User
Junction-37788 | 357065.2773 | 6666057.4648 | 31.4044 | Junction
Junction-37844 | 357667.1992 | 6667925.8828 | 8.5531 | Junction
Junction-37845 | 357667.0273 | 6667928.0352 | 8.5797 | Junction
Junction-37884 | 359477.0156 | 6667550.4492 | 14.218 | Sink/User
Junction-37885 | 359472.2305 | 6667557.7344 | 14.6459 | Junction
Junction-38006 | 357214.832 | 6666136 | 30.0753 | Junction
Junction-38195 | 357173.7344 | 6669311.6914 | 31.6761 | Junction
Junction-38245 | 358069.4844 | 6666475.3242 | 29.0365 | Junction
Junction-38294 | 357855.8594 | 6666259.2422 | 28.5852 | Junction
Junction-38343 | 362871.543 | 6673016.2578 | 20.5889 | Sink/User
Junction-38353 | 357089.2227 | 6669346.6172 | 38.1287 | Junction
Junction-38356 | 357109.2148 | 6669358.5312 | 36.7726 | Junction
Junction-38425 | 362881.5859 | 6672995.7695 | 18.8359 | Junction
Junction-38427 | 362845.7227 | 6672826.4219 | 18.6324 | Sink/User
Junction-38429 | 362758.1289 | 6672911.0547 | 18.5349 | Sink/User
Junction-38449 | 357050.3594 | 6669324.625 | 41.7889 | Junction
Junction-38460 | 357362.9609 | 6669502.5234 | 36.0431 | Junction
Junction-38463 | 357364.7031 | 6669494.1641 | 34.7555 | Junction
Junction-38492 | 357221.9336 | 6669411.6797 | 31.2698 | Junction
Junction-38586 | 358135.7031 | 6666255.0742 | 11.3118 | Junction
Junction-38595 | 358072.1758 | 6666467.9844 | 29.6021 | Sink/User
Junction-38652 | 357258.875 | 6669294.2734 | 29.9268 | Junction
Junction-38706 | 357128.75 | 6669294.1641 | 36.9468 | Sink/User
Junction-38786 | 357196.707 | 6669404.2617 | 31.8791 | Junction
Junction-38803 | 357207.0039 | 6669407.832 | 31.8597 | Junction
Junction-38805 | 357197.6484 | 6669317.9727 | 30.0745 | Junction
Junction-38817 | 357021.7383 | 6669242.2695 | 40.6735 | Junction
Junction-38905 | 357188.3203 | 6669329.5781 | 30.4636 | Sink/User
Junction-39039 | 366223.7148 | 6670109.4961 | 19.8855 | Sink/User
Junction-39059 | 357284.2383 | 6669168.3867 | 22.0048 | Junction
Junction-39069 | 357276.4023 | 6669219.1953 | 26.1679 | Junction
Junction-39113 | 358170.082 | 6666214.3477 | 6.7465 | Sink/User
Junction-39122 | 357294.1367 | 6669256.5703 | 27.2994 | Junction
Junction-39145 | 362829.4727 | 6672932.5 | 18.3335 | Junction
Junction-39150 | 357400.6016 | 6668486.793 | 20.2549 | Sink/User
Junction-39152 | 357398.2031 | 6668491.7969 | 20.2105 | Junction
Junction-39156 | 357382.8477 | 6668519.4727 | 20.0484 | Junction
Junction-39409 | 357158.5117 | 6669478.9531 | 47.1267 | Junction
Junction-39719 | 357234.7617 | 6666158.3047 | 28.9968 | Junction
Junction-39721 | 357240.8867 | 6666168.2812 | 29.3915 | Junction
Junction-40767 | 359381.582 | 6667376.418 | 20.745 | Junction
Junction-40770 | 357170.7812 | 6668010.9922 | 21.7052 | Sink/User
Junction-40791 | 357146.875 | 6668032.375 | 25.7022 | Junction
Junction-40794 | 357221.7266 | 6666177.3125 | 25.9514 | Sink/User
Junction-40889 | 360107.0664 | 6668528.9258 | 17.0544 | Junction
Junction-40892 | 358726.1055 | 6667756.6016 | 30.2957 | Sink/User
Junction-40961 | 362428.125 | 6671385.4258 | 18.1704 | Junction
Junction-41008 | 357151.1523 | 6668440.8242 | 23.3122 | Junction
Junction-41026 | 357777.3867 | 6667782.3828 | 8.4649 | Junction
Junction-41031 | 357801.9844 | 6667719.4375 | 8.5114 | Junction
Junction-41049 | 357852.5625 | 6666165.2852 | 19.9799 | Sink/User
Junction-41058 | 357847.8867 | 6666157.5508 | 18.5675 | Junction
Junction-41060 | 360072.4805 | 6668665.3047 | 27.3295 | Sink/User
Junction-41082 | 358724.4023 | 6667799.2969 | 29.8185 | Junction
Junction-41095 | 359354.0117 | 6667346.5273 | 26.0873 | Sink/User
Junction-41107 | 357206.6367 | 6666147.7461 | 27.5869 | Sink/User
Junction-41132 | 363449.9414 | 6672345.168 | 15.6833 | Junction
Junction-41266 | 355548.9531 | 6664543.8242 | 20.4729 | Sink/User
Junction-41284 | 363024.5586 | 6671433.4102 | 18.3713 | Sink/User
Junction-41442 | 363778.2695 | 6671008.0703 | 7.5467 | Junction
Junction-41523 | 363801.2227 | 6671052.5234 | 7.5775 | Junction
Junction-41572 | 355630.3906 | 6664575.9062 | 20.4885 | Junction
Junction-41577 | 355623.6641 | 6664579.7305 | 19.7679 | Junction
Junction-41582 | 355569.0273 | 6664609.832 | 13.2547 | Junction
Junction-41587 | 355453.3242 | 6664607.3359 | 8.3956 | Junction
Junction-41619 | 357034.3594 | 6668849.6523 | 20.6213 | Junction
Junction-41620 | 357035.5898 | 6668835.707 | 20.5161 | Sink/User
Junction-41683 | 355524.0352 | 6664664.4297 | 10.6243 | Junction
Junction-41711 | 357018.6836 | 6668856.6758 | 20.0168 | Sink/User
Junction-41716 | 357271.5586 | 6666122.8594 | 36.2217 | Sink/User
Junction-41740 | 355564.9414 | 6664613.1992 | 12.9338 | Junction
Junction-41940 | 358098.2383 | 6667485.4609 | 4.3885 | Sink/User
Junction-42099 | 363746.668 | 6671086.9023 | 7.937 | Junction
Junction-42173 | 363148.1055 | 6672419.8008 | 21.2921 | Sink/User
Junction-42178 | 363303.4492 | 6672182.0703 | 20.9485 | Sink/User
Junction-42312 | 363260.8906 | 6672183.6055 | 18.1322 | Junction
Junction-42407 | 363800.0156 | 6670974.1523 | 5.9025 | Junction
Junction-42686 | 355630.6641 | 6664588.7148 | 19.1949 | Sink/User
Junction-42748 | 357374.1211 | 6668541.4219 | 20.6611 | Sink/User
Junction-42761 | 363261.9609 | 6672178.1875 | 18.029 | Junction
Junction-42763 | 357184.8477 | 6666099.9531 | 31.1522 | Sink/User
Junction-43191 | 358668.5 | 6667842.0156 | 30.9157 | Junction
Junction-43562 | 357026.1211 | 6666035.7773 | 27.1444 | Sink/User
Junction-43566 | 357023.8281 | 6666016.5469 | 26.8019 | Junction
Junction-43595 | 363825.6992 | 6671000.1406 | 6.0308 | Sink/User
Junction-44635 | 358691.9883 | 6667845.0508 | 30.5595 | Sink/User
Junction-44920 | 357933.2734 | 6667710.25 | 7.5324 | Junction
Junction-45254 | 357415.3125 | 6669539.3672 | 38.3873 | Sink/User
Junction-45717 | 357030.4062 | 6668420.9922 | 25.8612 | Junction
Junction-45888 | 357388.1328 | 6669499.7773 | 35.1004 | Junction
Junction-45979 | 363484.9219 | 6672368.7656 | 15.9086 | Sink/User
Junction-46121 | 357042.4336 | 6666009.6562 | 28.4372 | Junction
Junction-46129 | 357511.4492 | 6668046.5859 | 21.0024 | Sink/User
Junction-46131 | 363418.4531 | 6671361.0742 | 8.2868 | Junction
Junction-46212 | 356837.6953 | 6665835.6016 | 17.968 | Sink/User
Junction-46214 | 356846.8398 | 6665839.2109 | 19.3038 | Junction
Junction-46217 | 356868.7656 | 6665856.0234 | 21.4352 | Sink/User
Junction-46223 | 356842.8359 | 6665848.8047 | 19.3157 | Junction
Junction-46225 | 357070.625 | 6665995.7891 | 30.9729 | Sink/User
Junction-46228 | 356842.8086 | 6665855.9414 | 19.5025 | Junction
Junction-46597 | 362554.1094 | 6671361.7305 | 18.2094 | Sink/User
Junction-46680 | 357391.2266 | 6669236.6172 | 23.5078 | Junction
Junction-46849 | 357049.2695 | 6665991.8164 | 28.7142 | Junction
Junction-46923 | 356842.7773 | 6665864.3906 | 19.5262 | Junction
Junction-47050 | 357042.0469 | 6669223.8242 | 38.7366 | Junction
Junction-47051 | 357045.1797 | 6669221.9453 | 38.5066 | Junction
Junction-47088 | 357511.3516 | 6668058.2656 | 20.1508 | Junction
Junction-47090 | 360257.4258 | 6668593.9766 | 20.1384 | Junction
Junction-47093 | 356850.7891 | 6665796.3633 | 17.4756 | Sink/User
Junction-47223 | 363405.9453 | 6671349.707 | 8.6921 | Sink/User
Junction-47600 | 363261.7773 | 6671339.2148 | 11.6148 | Junction
Junction-47603 | 357764.957 | 6666432.5 | 29.3297 | Sink/User
Junction-47851 | 357051.6406 | 6666040.457 | 30.6883 | Sink/User
Junction-47852 | 357057.0625 | 6666039.3203 | 31.4647 | Junction
Junction-47855 | 356873.125 | 6665870.9453 | 21.8461 | Sink/User
Junction-47904 | 358973.625 | 6667794.4023 | 24.052 | Junction
Junction-47934 | 356981.4336 | 6665988.168 | 24.311 | Junction
Junction-47936 | 356986.1914 | 6665989.543 | 24.4452 | Junction
Junction-48140 | 357401.2344 | 6669324.5195 | 26.2816 | Junction
Junction-48274 | 356996.9922 | 6669183.0391 | 33.5333 | Junction
Junction-48312 | 357037.0273 | 6669460.3242 | 52.2443 | Sink/User
Junction-48315 | 357035.7422 | 6669445.4102 | 53.3384 | Junction
Junction-48318 | 357062.0391 | 6665927.6953 | 32.8006 | Sink/User
Junction-48324 | 357039.0508 | 6665934.6602 | 29.8808 | Junction
Junction-48555 | 357764.7969 | 6666340.293 | 32.0399 | Junction
Junction-48557 | 360263.1172 | 6668583.9102 | 20.5419 | Sink/User
Junction-48626 | 357445.043 | 6669319 | 23.4803 | Sink/User
Junction-48688 | 356955.4453 | 6665827.2773 | 27.0758 | Junction
Junction-48934 | 362814.457 | 6672930.3828 | 18.7523 | Junction
Junction-49024 | 357048.9727 | 6665974.6562 | 28.6869 | Junction
Junction-49026 | 357049.2109 | 6666003.6211 | 29.1061 | Junction
Junction-49052 | 356868.0312 | 6665798.957 | 19.5573 | Junction
Junction-49141 | 356879.5156 | 6665741.5391 | 21.1887 | Sink/User
Junction-49142 | 356885.0625 | 6665738.7422 | 22.0433 | Junction
Junction-49190 | 357805.8945 | 6666185.8359 | 23.0347 | Junction
Junction-49267 | 357000.6719 | 6669178.0938 | 32.9518 | Sink/User
Junction-49268 | 357088.4727 | 6669346.1719 | 38.1904 | Junction
Junction-49349 | 356759.375 | 6668033.9023 | 18.6761 | Junction
Junction-49413 | 356867.5469 | 6665800.2383 | 19.5446 | Junction
Junction-49415 | 356973.9531 | 6665970.6406 | 27.6312 | Sink/User
Junction-49563 | 357037.0781 | 6666005.707 | 27.9767 | Sink/User
Junction-49604 | 356895.875 | 6665753.3516 | 21.497 | Junction
Junction-49754 | 356850.4453 | 6665832.7461 | 19.3731 | Junction
Junction-49757 | 356863.4688 | 6665809.5195 | 19.4338 | Junction
Junction-49794 | 357112.4609 | 6669344.0781 | 36.0238 | Sink/User
Junction-49938 | 356975.4961 | 6665986.8711 | 24.376 | Junction
Junction-50025 | 357016.0898 | 6665888.2773 | 30.1404 | Junction
Junction-50028 | 361828.7969 | 6669118.8945 | 7.0123 | Sink/User
Junction-50187 | 356877.3203 | 6665820.8555 | 20.875 | Sink/User
Junction-50272 | 358010.6641 | 6666191.418 | 11.2075 | Junction
Junction-50281 | 357037.1797 | 6668281.6367 | 23.1104 | Junction
Junction-50282 | 357030.9648 | 6668278.7031 | 23.8948 | Junction
Junction-50299 | 357046.9492 | 6665887.4688 | 34.0192 | Sink/User
Junction-50328 | 357066.3555 | 6665976.0391 | 30.3982 | Sink/User
Junction-50392 | 356839.0312 | 6665821.0859 | 17.2616 | Sink/User
Junction-50404 | 358918.6875 | 6667772.0625 | 19.9808 | Junction
Junction-50461 | 356880.5547 | 6665808.1328 | 20.8171 | Sink/User
Junction-50470 | 358900.75 | 6667799.8242 | 22.0142 | Sink/User
Junction-50543 | 363490.8086 | 6672329.7266 | 14.7197 | Junction
Junction-50652 | 356833.7617 | 6665866.6562 | 18.3702 | Sink/User
Junction-50786 | 356995.8789 | 6667376.0312 | 9.8397 | Sink/User
Junction-50787 | 356987.5117 | 6667374.5391 | 10.3957 | Junction
Junction-50972 | 357068.0117 | 6669291.0625 | 41.7245 | Sink/User
Junction-50999 | 356934.957 | 6665812.5 | 25.496 | Junction
Junction-51026 | 357832.0508 | 6666301.2188 | 26.9837 | Junction
Junction-51044 | 357021.5898 | 6665898.043 | 30.0882 | Junction
Junction-51072 | 357010.2695 | 6667286.6875 | 11.6717 | Junction
Junction-51163 | 356904.6602 | 6665849.3984 | 23.7994 | Sink/User
Junction-51508 | 357639.0469 | 6666434.6328 | 39.4627 | Sink/User
Junction-51524 | 357055.3203 | 6667304.5156 | 10.6943 | Junction
Junction-51548 | 356996.6523 | 6665984.0586 | 26.1178 | Sink/User
Junction-51620 | 358790.9609 | 6667820.8281 | 33.6933 | Junction
Junction-51622 | 358791.5938 | 6667819.5781 | 33.5807 | Junction
Junction-51625 | 358798.2617 | 6667789.6133 | 30.7358 | Junction
Junction-51737 | 357098.3477 | 6667301.7539 | 10.8968 | Junction
Junction-51815 | 357037.1562 | 6668302.5547 | 21.8791 | Sink/User
Junction-52026 | 357038.0664 | 6665868.8711 | 34.0706 | Sink/User
Junction-52250 | 357007.543 | 6666029.6328 | 24.0305 | Sink/User
Junction-52254 | 357020.918 | 6666015.8203 | 26.565 | Junction
Junction-52417 | 358046.7383 | 6666165.9336 | 6.4629 | Sink/User
Junction-52634 | 358074.5859 | 6666235.6992 | 11.1749 | Junction
Junction-52874 | 358988.5859 | 6667769.0703 | 26.2385 | Sink/User
Junction-52880 | 357112.3516 | 6669205.4688 | 34.3192 | Sink/User
Junction-52889 | 357632.6484 | 6666397.1797 | 38.5166 | Junction
Junction-53505 | 358790.8047 | 6667780.625 | 30.4452 | Junction
Junction-53612 | 359182.2109 | 6667795.168 | 36.3792 | Junction
Junction-53615 | 357296.1641 | 6669138.1211 | 20.2609 | Junction
Junction-53865 | 363114.8594 | 6671755.1133 | 18.0964 | Junction
Junction-53866 | 363114.875 | 6671755.4922 | 18.0913 | Sink/User
Junction-53867 | 363114.8398 | 6671754.75 | 18.1015 | Sink/User
Junction-54075 | 358114.0195 | 6666201.9141 | 7.0118 | Sink/User
Junction-54115 | 359531.2969 | 6667643.4648 | 15.1688 | Junction
Junction-54118 | 359487.25 | 6667644.0547 | 15.286 | Junction
Junction-54119 | 358802.2656 | 6667789.9141 | 30.7121 | Sink/User
Junction-54121 | 358804.6406 | 6667821.0117 | 34.5794 | Sink/User
Junction-54123 | 358781.75 | 6667822.5312 | 32.9887 | Sink/User
Junction-54179 | 359459.0547 | 6667392.4922 | 13.5446 | Junction
Junction-54387 | 356968.9961 | 6666004.3867 | 21.5747 | Sink/User
Junction-54599 | 358078.4453 | 6666225.8242 | 9.5347 | Junction
Junction-54634 | 359193.7773 | 6667810.9219 | 37.2362 | Sink/User
Junction-54809 | 359584.2969 | 6667693.9375 | 16.3594 | Sink/User
Junction-54877 | 363154.0547 | 6672488.1289 | 19.8843 | Junction
Junction-54882 | 357059.7305 | 6669367.6758 | 41.4749 | Sink/User
Junction-54909 | 357092.1016 | 6669206.5273 | 35.0112 | Junction
Junction-54948 | 357008.8125 | 6667255.8594 | 11.702 | Sink/User
Junction-55173 | 357094.168 | 6669200.1875 | 34.2983 | Sink/User
Junction-55177 | 357273.2227 | 6669467.3828 | 36.6212 | Sink/User
Junction-55179 | 363156.1289 | 6672473.1719 | 19.9569 | Sink/User
Junction-55365 | 363108.5586 | 6672475.5508 | 21.8162 | Junction
Junction-55565 | 357577.2891 | 6668334.957 | 16.9467 | Junction
Junction-55566 | 357583.4023 | 6668336.7422 | 17.0315 | Junction
Junction-55861 | 357427.0547 | 6668649.5586 | 26.0502 | Junction
Junction-56012 | 357145.3125 | 6669380.1133 | 34.699 | Junction
Junction-56146 | 357468.6523 | 6667475.0898 | 7.5824 | Junction
Junction-56147 | 357468.3984 | 6667472.3086 | 7.5457 | Sink/User
Junction-56361 | 359016.5234 | 6667117.3672 | 12.7189 | Junction
Junction-56779 | 357384.8711 | 6669490.2188 | 33.5638 | Sink/User
Junction-56780 | 357382.8906 | 6669498.5078 | 34.9695 | Junction
Junction-57062 | 362931.2031 | 6673037.4727 | 19.7305 | Junction
Junction-57301 | 362784.793 | 6672978.3438 | 18.7398 | Sink/User
Junction-57893 | 358786.5977 | 6667791.6445 | 30.8926 | Junction
Junction-58481 | 357132.4336 | 6669399.6641 | 37.8777 | Sink/User
Junction-58617 | 361886.082 | 6668482.1758 | 13.6685 | Sink/User
Junction-58647 | 357150.7773 | 6669427.1094 | 39.3017 | Sink/User
Junction-58769 | 359001.0742 | 6667116.6641 | 11.2452 | Sink/User
Junction-58780 | 357174.332 | 6669394.8828 | 31.3484 | Junction
Junction-58784 | 357356.1367 | 6669473.3828 | 32.0776 | Sink/User
Junction-58790 | 357339.8438 | 6669487.1289 | 34.856 | Junction
Junction-59203 | 361934.0977 | 6669132.0039 | 2.5579 | Junction
Junction-59693 | 359023.3125 | 6667090.9531 | 9.244 | Junction
Junction-60463 | 357091.4219 | 6669208.5938 | 35.2429 | Junction
Junction-60532 | 357390.2969 | 6669500.4492 | 35.1671 | Junction
Junction-60533 | 357388.4805 | 6669506.707 | 36.0724 | Junction
Junction-60613 | 357695.7773 | 6667751.5508 | 8.3253 | Junction
Junction-60758 | 357127.3828 | 6669506.5469 | 50.1752 | Sink/User
Junction-61093 | 357731.5 | 6668477.1836 | 32.9488 | Junction
Junction-61715 | 357115.8008 | 6669470.293 | 47.4974 | Junction
Junction-61767 | 357060.6875 | 6669457.4297 | 50.7693 | Junction
Junction-61769 | 357084.4648 | 6669496.9609 | 48.3448 | Sink/User
Junction-63624 | 357192.4492 | 6669318.1094 | 30.2755 | Junction
Junction-63760 | 357071.9648 | 6669441.5 | 50.8493 | Sink/User
Junction-63769 | 357337.2734 | 6669443.0977 | 30.444 | Sink/User
Junction-64013 | 357402.9141 | 6668527.5547 | 20.1514 | Junction
Junction-64021 | 356829.7773 | 6668030.7109 | 18.1974 | Junction
Junction-64134 | 357756.0352 | 6667606.4727 | 9.4616 | Junction
Junction-64230 | 357378.7461 | 6669287.5195 | 26.6081 | Sink/User
Junction-64275 | 357305.1406 | 6669416.9297 | 29.6788 | Junction
Junction-64662 | 357390.4492 | 6669279.2109 | 25.4786 | Junction
Junction-64664 | 357371.2695 | 6669536.1602 | 40.0064 | Sink/User
Junction-64665 | 357369.2461 | 6669507.3359 | 36.5501 | Junction
Junction-64780 | 363253.043 | 6672313.6133 | 18.9322 | Sink/User
Junction-64781 | 363248.4258 | 6672307.0938 | 18.8273 | Junction
Junction-65234 | 357331.7695 | 6669409.3633 | 28.1761 | Junction
Junction-65236 | 357293.1055 | 6669170.6758 | 21.9052 | Sink/User
Junction-65240 | 357265.1719 | 6669461.1406 | 36.0677 | Sink/User
Junction-65373 | 357094.0195 | 6669467.9258 | 48.2831 | Junction
Junction-65376 | 357289.7852 | 6669226.7461 | 26.0217 | Sink/User
Junction-65389 | 359627.6172 | 6667680.3047 | 17.1124 | Junction
Junction-65422 | 357059.9727 | 6669483.0508 | 48.93 | Sink/User
Junction-65528 | 357013.8906 | 6668050.6797 | 18.7777 | Junction
Junction-65680 | 357350.2383 | 6669525.0938 | 39.2063 | Sink/User
Junction-65709 | 358766.5742 | 6667769.7031 | 30.3457 | Sink/User
Junction-65818 | 363083.5859 | 6672543.7734 | 19.4826 | Junction
Junction-66224 | 359644.8242 | 6667823.043 | 18.0715 | Junction
Junction-66227 | 359575.0391 | 6667788.1641 | 18.0319 | Sink/User
Junction-66516 | 357170.168 | 6669469.7031 | 45.148 | Sink/User
Junction-66675 | 362713.0469 | 6670992.7461 | 16.9682 | Junction
Junction-67029 | 357407.3867 | 6669495.8281 | 33.9538 | Sink/User
Junction-67935 | 363057.4883 | 6672532.6641 | 21.0159 | Sink/User
Junction-67964 | 357224.3867 | 6669449.832 | 36.3222 | Sink/User
Junction-67965 | 357227.3047 | 6669447.4414 | 35.8344 | Junction
Junction-67966 | 357227.5039 | 6669449.9258 | 36.1502 | Sink/User
Junction-68672 | 357090.8867 | 6669394.4336 | 41.0705 | Sink/User
Junction-68862 | 357060.1406 | 6669330.168 | 40.8106 | Junction
Junction-68937 | 359595.0391 | 6667777.2305 | 17.5295 | Junction
Junction-68938 | 359590.8906 | 6667772.8906 | 17.5059 | Junction
Junction-69578 | 357973.7344 | 6667441.0977 | 7.9167 | Junction
Junction-70718 | 357302.6719 | 6669417.1445 | 29.82 | Junction
Junction-71596 | 363192.3906 | 6672341.5508 | 19.7036 | Junction
Junction-71599 | 359915.9805 | 6667866.1758 | 25.0948 | Sink/User
Junction-71707 | 359916.7578 | 6667842.6172 | 25.1912 | Junction
Junction-72077 | 359989.0859 | 6667854.3594 | 23.5364 | Sink/User
Junction-72630 | 363115.1562 | 6672458.7773 | 22.7118 | Junction
Junction-72632 | 363055.2656 | 6672370.6367 | 25.7131 | Sink/User
Junction-73054 | 363119.3828 | 6672277.3086 | 20.8056 | Junction
Junction-73056 | 363103.1641 | 6672216.5078 | 20.4009 | Sink/User
Junction-73295 | 357760.75 | 6667631.0039 | 10.2777 | Sink/User
Junction-73296 | 357750.8867 | 6667642.5 | 10.9138 | Junction
Junction-73297 | 357753.5391 | 6667643.5391 | 10.9109 | Sink/User
Junction-73674 | 357974.707 | 6667398.1133 | 7.3561 | Sink/User
Junction-74257 | 363014.9688 | 6672727.6914 | 18.1134 | Junction
Junction-74258 | 362989.082 | 6672801.6406 | 20.6909 | Junction
Junction-74498 | 357085.0664 | 6668421.625 | 23.8971 | Junction
Junction-74927 | 357418.5078 | 6668641.9023 | 25.6057 | Sink/User
Junction-75222 | 362977.5078 | 6672714.6289 | 19.4175 | Sink/User
Junction-75386 | 359881.9766 | 6667834.2773 | 24.501 | Junction
Junction-75387 | 359883.4102 | 6667831.9531 | 24.7085 | Junction
Junction-75388 | 359871.3828 | 6667778.3867 | 25.926 | Junction
Junction-75389 | 359872.1055 | 6667776.832 | 26.0691 | Sink/User
Junction-75752 | 359851.6367 | 6667807.6992 | 21.224 | Junction
Junction-75753 | 359838.6445 | 6667795.4648 | 20.6914 | Junction
Junction-76728 | 359981.2695 | 6667837.3984 | 23.2149 | Junction
Junction-76786 | 357574.1172 | 6667902.9219 | 10.5709 | Sink/User
Junction-76989 | 359872.9922 | 6667779.1758 | 25.9795 | Sink/User
Junction-77288 | 363118.0938 | 6672276.1992 | 20.829 | Junction
Junction-84173 | 362509.0859 | 6671404.8398 | 18.2057 | Junction
Junction-84540 | 357261.4766 | 6669293.9297 | 29.9135 | Sink/User
Junction-93415 | 362712.3672 | 6671647.9844 | 19.0185 | Sink/User
Junction-94512 | 362748.9883 | 6671632.2656 | 18.7393 | Junction
Junction-94517 | 362730.8477 | 6671599.2812 | 17.7028 | Junction
Junction-94616 | 363484.5 | 6672151.457 | 13.5198 | Junction
Junction-94619 | 363452.5352 | 6672045.4492 | 14.0772 | Sink/User
Junction-94894 | 362521.6602 | 6670914.9023 | 21.1073 | Sink/User
Junction-94950 | 362477.207 | 6671679.2773 | 18.44 | Junction
Junction-95020 | 362624.832 | 6671591.6133 | 17.8235 | Sink/User
Junction-95084 | 362434.1562 | 6671378.8008 | 17.9783 | Junction
Junction-95085 | 362432.0938 | 6671385 | 18.1439 | Junction
Junction-95215 | 362184.4062 | 6671761.8594 | 21.7369 | Junction
Junction-95216 | 362196.2969 | 6671728.6719 | 21.8266 | Junction
Junction-95240 | 362190.6289 | 6671724.2188 | 21.7925 | Junction
Junction-95242 | 362149.8047 | 6671741.7734 | 21.3604 | Sink/User
Junction-95284 | 362414.1055 | 6671480.8242 | 20.5612 | Junction
Junction-95285 | 362421.5469 | 6671453.6016 | 20.3013 | Junction
Junction-95286 | 362402.9102 | 6671477.5391 | 20.7692 | Sink/User
Junction-95354 | 362209.707 | 6671727.7773 | 21.9676 | Sink/User
Junction-95618 | 363229 | 6672314.0742 | 19.2172 | Junction
Junction-95634 | 362713.4375 | 6671605.7617 | 18.0385 | Junction
Junction-95635 | 362707.2109 | 6671578.0977 | 17.1118 | Sink/User
Junction-95940 | 363227.4492 | 6672315.0117 | 19.2419 | Junction
Junction-95942 | 363262.4844 | 6672396.3633 | 23.4218 | Sink/User
Junction-96222 | 357820.1016 | 6668417.9492 | 26.6281 | Junction
Junction-96224 | 357816.1289 | 6668389.457 | 24.3369 | Junction
Junction-96226 | 357712.3125 | 6668400.6602 | 22.2642 | Sink/User
Junction-96454 | 363438.4609 | 6672051.5781 | 14.8828 | Junction
Junction-96512 | 363401.5664 | 6671911.8008 | 13.5539 | Junction
Junction-96514 | 363397.9531 | 6671919.1445 | 13.9847 | Junction
Junction-96577 | 363489.4414 | 6672161.293 | 12.9227 | Junction
Junction-96634 | 362215.3086 | 6671670.3672 | 23.7833 | Junction
Junction-96635 | 362208.832 | 6671667.7617 | 23.7966 | Sink/User
Junction-96810 | 363630.7227 | 6671846.2266 | 9.5293 | Junction
Junction-96845 | 362415.0938 | 6671445.7891 | 20.2439 | Junction
Junction-96846 | 362411.7188 | 6671445.2891 | 20.2509 | Sink/User
Junction-96849 | 362422.8672 | 6671448.9766 | 20.2319 | Junction
Junction-96850 | 362433.0586 | 6671451.2109 | 20.0584 | Sink/User
Junction-96900 | 362491.1094 | 6670886.8047 | 20.3478 | Sink/User
Junction-96958 | 362430.5078 | 6671580.4922 | 21.3791 | Junction
Junction-96962 | 362636.3008 | 6670856.25 | 18.3953 | Junction
Junction-96963 | 362643.5938 | 6670851.7852 | 18.213 | Junction
Junction-97113 | 363218.543 | 6670962.3477 | 6.4923 | Sink/User
Junction-97159 | 363493.8125 | 6672190.0664 | 12.1738 | Junction
Junction-97160 | 363502.9922 | 6672187.4336 | 11.3607 | Sink/User
Junction-97180 | 363169.8438 | 6671594.1055 | 15.2502 | Junction
Junction-97299 | 363492.0469 | 6672146.3672 | 12.7253 | Sink/User
Junction-97373 | 362898.293 | 6671476.1758 | 16.4488 | Junction
Junction-97499 | 363409.8359 | 6671915.2344 | 13.2773 | Sink/User
Junction-97501 | 363832.6719 | 6671882.1289 | 23.6193 | Sink/User
Junction-97575 | 363593.0469 | 6672238.8555 | 8.4371 | Junction
Junction-97576 | 363677.5156 | 6672206.3125 | 9.5353 | Sink/User
Junction-97749 | 362759.5547 | 6671509.0703 | 15.0499 | Junction
Junction-97751 | 362811.7031 | 6671469.6836 | 15.0913 | Junction
Junction-97753 | 362884.3906 | 6671445.1484 | 15.2367 | Junction
Junction-97754 | 362919.4102 | 6671425.6641 | 17.7784 | Sink/User
Junction-97767 | 357022.5117 | 6668294.8359 | 23.79 | Junction
Junction-97769 | 357013.9727 | 6668296.3242 | 24.8588 | Sink/User
Junction-97770 | 357023.6172 | 6668275.2383 | 24.7733 | Junction
Junction-97774 | 357121.7539 | 6668035.8711 | 24.2393 | Sink/User
Junction-97775 | 357128.2031 | 6668017.0742 | 21.4754 | Junction
Junction-97898 | 363081.5469 | 6671627.207 | 19.2468 | Sink/User
Junction-97918 | 363085.9141 | 6672453.0664 | 24.4112 | Sink/User
Junction-97934 | 357643.3281 | 6668288.8516 | 15.5911 | Junction
Junction-97937 | 357645.6914 | 6668166.4219 | 12.9105 | Junction
Junction-97993 | 362460.2852 | 6671350.1602 | 17.4839 | Sink/User
Junction-97997 | 362382.0078 | 6671375.0469 | 18.3417 | Sink/User
Junction-98040 | 357123.668 | 6667883.9023 | 15.3839 | Junction
Junction-98224 | 362876.0625 | 6671175.2617 | 15.0094 | Junction
Junction-98228 | 362966.7383 | 6671456.6406 | 18.6168 | Sink/User
Junction-98243 | 363060.2656 | 6671521.8711 | 22.3518 | Junction
Junction-98261 | 362647.4727 | 6670858.418 | 18.0952 | Sink/User
Junction-98262 | 362640.9414 | 6670847.9688 | 18.2555 | Sink/User
Junction-98264 | 362631.7461 | 6670798.2461 | 17.9425 | Sink/User
Junction-98390 | 362401.7969 | 6671594.4883 | 21.1249 | Sink/User
Junction-98397 | 363396.2305 | 6671916.3008 | 13.9456 | Junction
Junction-98399 | 363408.0312 | 6671868.3125 | 12.0186 | Sink/User
Junction-98413 | 363248.1758 | 6672176.9141 | 19.3064 | Sink/User
Junction-98461 | 362678.9375 | 6671124.875 | 16.6399 | Sink/User
Junction-98465 | 362685.9062 | 6671076.4648 | 16.8527 | Junction
Junction-98582 | 363258.6758 | 6671553.2422 | 11.5918 | Sink/User
Junction-98583 | 363232.8984 | 6671499.1133 | 12.098 | Sink/User
Junction-98673 | 363246.5 | 6671517.3789 | 11.7072 | Junction
Junction-98676 | 363056.6172 | 6671513.9727 | 22.0455 | Sink/User
Junction-98710 | 357832.3555 | 6667456.1133 | 8.6976 | Junction
Junction-98717 | 356968.1758 | 6668453.5703 | 30.536 | Junction
Junction-98718 | 356966.7109 | 6668471.2578 | 30.8922 | Sink/User
Junction-98719 | 356973.5117 | 6668453.5898 | 29.8362 | Junction
Junction-98720 | 356975.668 | 6668442.4453 | 29.0989 | Junction
Junction-98721 | 356971.0078 | 6668441.0938 | 29.6106 | Sink/User
Junction-98722 | 356968.0859 | 6668410.0273 | 28.8201 | Junction
Junction-98723 | 356972.4141 | 6668395.0391 | 29.0307 | Junction
Junction-98724 | 357009.5664 | 6668413.0469 | 26.3345 | Junction
Junction-98725 | 357003.0547 | 6668426.0664 | 26.692 | Sink/User
Junction-98729 | 357844.8359 | 6668972.2227 | 18.8674 | Sink/User
Junction-98765 | 357336.3398 | 6668455.6914 | 20.5199 | Sink/User
Junction-98830 | 359700.6992 | 6667776.793 | 18.4446 | Junction
Junction-98833 | 357975.2773 | 6668472.6055 | 22.7923 | Sink/User
Junction-98841 | 358014.2148 | 6668519.5508 | 21.8011 | Junction
Junction-98844 | 357529.1094 | 6667936.1211 | 18.588 | Sink/User
Junction-98849 | 357492.1367 | 6667984.0898 | 24.6392 | Junction
Junction-98858 | 357058.6992 | 6668037.4375 | 19.0721 | Sink/User
Junction-98860 | 357046.207 | 6668020.3164 | 18.7801 | Junction
Junction-98867 | 357561 | 6668165.0039 | 14.4932 | Junction
Junction-98869 | 357643.8438 | 6668122.1602 | 13.1603 | Junction
Junction-98870 | 357632.0859 | 6668122.2227 | 13.3836 | Sink/User
Junction-98873 | 357661.6602 | 6668009.7305 | 10.4116 | Junction
Junction-98874 | 357627.9922 | 6668006.7422 | 11.0548 | Junction
Junction-98875 | 357625.4297 | 6668014.043 | 11.6918 | Sink/User
Junction-98876 | 357626.6523 | 6667999.4453 | 10.7009 | Sink/User
Junction-98878 | 357664.1406 | 6667962.2578 | 8.9834 | Junction
Junction-98879 | 357671.3477 | 6667962.7383 | 8.9139 | Sink/User
Junction-98881 | 357630.4922 | 6667959.6133 | 9.0994 | Sink/User
Junction-98882 | 357664.0781 | 6667963.6641 | 9.0114 | Junction
Junction-98907 | 357526.5078 | 6668162.6875 | 15.1729 | Junction
Junction-98908 | 357524.5977 | 6668169.2812 | 15.1783 | Sink/User
Junction-98909 | 357536.7734 | 6668163.582 | 15.0164 | Junction
Junction-98910 | 357537.9102 | 6668146.4258 | 15.1735 | Sink/User
Junction-98912 | 357501.8203 | 6668179.2109 | 15.2008 | Sink/User
Junction-98919 | 359509.7695 | 6667756.668 | 16.2388 | Sink/User
Junction-98922 | 359481.8125 | 6667564.0547 | 14.2009 | Junction
Junction-98926 | 357085.9453 | 6668412.5312 | 23.3736 | Junction
Junction-98927 | 357082.2461 | 6668412.4805 | 23.5151 | Sink/User
Junction-98936 | 357357.1016 | 6668507.5977 | 20.1829 | Junction
Junction-99004 | 357867.4453 | 6668521.0508 | 33.3661 | Sink/User
Junction-99006 | 356870.8945 | 6668047.2539 | 18.4329 | Junction
Junction-99010 | 356924.75 | 6667985.418 | 18.3558 | Junction
Junction-99013 | 356967.8203 | 6667994.5117 | 18.5463 | Sink/User
Junction-99018 | 357513.375 | 6667430.4844 | 6.7606 | Junction
Junction-99019 | 357523.0195 | 6667429.3438 | 6.7538 | Junction
Junction-99032 | 359665.5508 | 6667725.3828 | 17.6994 | Junction
Junction-99048 | 357674.5391 | 6667857.6875 | 8.3388 | Junction
Junction-99051 | 357698.1289 | 6667825.6055 | 8.2198 | Sink/User
Junction-99052 | 357681.5312 | 6667826.3594 | 8.3065 | Junction
Junction-99053 | 357624.2734 | 6667613.7734 | 8.423 | Junction
Junction-99054 | 357628.5586 | 6667623.668 | 8.5963 | Sink/User
Junction-99073 | 356818.1406 | 6668011.2109 | 17.9365 | Junction
Junction-99074 | 356819.9961 | 6668005.4023 | 17.8671 | Sink/User
Junction-99075 | 356828.2734 | 6668032.3906 | 18.2438 | Junction
Junction-99076 | 356830.6719 | 6668040.1055 | 18.4079 | Sink/User
Junction-99077 | 356820.2891 | 6668041.3008 | 18.4913 | Sink/User
Junction-99079 | 356856.9688 | 6668022.1055 | 17.9056 | Sink/User
Junction-99080 | 356853.2734 | 6668040.1641 | 18.334 | Junction
Junction-99081 | 356857.7383 | 6668062.918 | 19.2779 | Sink/User
Junction-99082 | 356882.3164 | 6668030.8945 | 17.9552 | Sink/User
Junction-99083 | 356804.8047 | 6668443.668 | 30.4552 | Junction
Junction-99084 | 356819.3242 | 6668460.4219 | 29.3476 | Sink/User
Junction-99085 | 356800.1602 | 6668456.9688 | 29.2477 | Sink/User
Junction-99087 | 356794.6719 | 6668418.5078 | 31.5103 | Sink/User
Junction-99088 | 356810.7695 | 6668426.4062 | 31.31 | Junction
Junction-99089 | 356816.0273 | 6668413.5039 | 31.6551 | Junction
Junction-99090 | 356827.9648 | 6668418.2852 | 31.5995 | Sink/User
Junction-99093 | 356816.1289 | 6668376.2383 | 31.7767 | Sink/User
Junction-99094 | 356846.2812 | 6668355.6406 | 30.9876 | Junction
Junction-99095 | 356840.918 | 6668353.7422 | 31.0135 | Sink/User
Junction-99096 | 356850.543 | 6668353.8711 | 30.8643 | Sink/User
Junction-99110 | 357644.4805 | 6668166.207 | 12.9194 | Junction
Junction-99111 | 357152.2969 | 6668294.8047 | 21.0608 | Junction
Junction-99114 | 357403.6602 | 6668015.082 | 27.9822 | Junction
Junction-99115 | 357387.8555 | 6668011.9727 | 28.4263 | Junction
Junction-99119 | 357325.1914 | 6668055.1992 | 28.5732 | Sink/User
Junction-99121 | 357330.3086 | 6668056.7148 | 28.4701 | Junction
Junction-99130 | 357491.3242 | 6668050.3008 | 22.2415 | Junction
Junction-99133 | 357537.1172 | 6668066.6211 | 18.2594 | Junction
Junction-99182 | 357098.4102 | 6667304.1406 | 10.8285 | Junction
Junction-99186 | 356884.9531 | 6668368.1523 | 30.3094 | Sink/User
Junction-99198 | 357730.1484 | 6668116.8281 | 15.3216 | Sink/User
Junction-99226 | 357453.0625 | 6668433.8008 | 19.7843 | Junction
Junction-99237 | 357073.8516 | 6668291.4883 | 21.009 | Junction
Junction-99238 | 357073.9062 | 6668292.6328 | 20.9536 | Sink/User
Junction-99247 | 359630.3164 | 6667677.4414 | 17.0408 | Sink/User
Junction-99277 | 357292.207 | 6668455.0508 | 20.9363 | Junction
Junction-99278 | 357297.5703 | 6668454.582 | 20.8653 | Junction
Junction-99286 | 357697.9844 | 6667517.9609 | 8.8486 | Sink/User
Junction-99292 | 357672.5664 | 6667568.0039 | 11.7973 | Sink/User
Junction-99304 | 357097.9375 | 6667195.1641 | 11.6604 | Junction
Junction-99307 | 357839.3555 | 6667675.5625 | 8.5179 | Sink/User
Junction-99319 | 357398.1719 | 6667374.5 | 5.99 | Junction
Junction-99321 | 357380.6797 | 6667416.2227 | 6.5068 | Junction
Junction-99323 | 357620.9922 | 6667609.3438 | 8.2748 | Sink/User
Junction-99326 | 357918.043 | 6667453.7539 | 9.1267 | Junction
Junction-99330 | 357058.6211 | 6668424.7539 | 25.055 | Junction
Junction-99350 | 357604.8164 | 6668348.3867 | 17.5464 | Junction
Junction-99351 | 357635.6641 | 6668372.6016 | 19.6126 | Sink/User
Junction-99360 | 357270.207 | 6668457.9375 | 21.1657 | Junction
Junction-99361 | 357268.7383 | 6668449.6562 | 21.4853 | Sink/User
Junction-99363 | 357285.7383 | 6668461.8242 | 20.7996 | Sink/User
Junction-99364 | 357284.8555 | 6668455.6992 | 21.0284 | Junction
Junction-99368 | 357157.4531 | 6668476.457 | 22.9004 | Junction
Junction-99373 | 357366.1328 | 6667758.9023 | 12.0955 | Sink/User
Junction-99375 | 357381.7227 | 6667764.7812 | 12.9137 | Junction
Junction-99376 | 357356.0078 | 6667809.7891 | 15.8042 | Junction
Junction-99377 | 357358.168 | 6667811.5156 | 15.965 | Sink/User
Junction-99395 | 357449.2422 | 6668028.2148 | 25.7783 | Junction
Junction-99424 | 357340.2031 | 6667826.8281 | 17.0649 | Sink/User
Junction-99438 | 357601.5547 | 6668344.832 | 17.394 | Junction
Junction-99461 | 356843.3789 | 6668368.4492 | 31.3286 | Junction
Junction-99462 | 356833.1484 | 6668370.0469 | 31.4797 | Junction
Junction-99463 | 356818.5586 | 6668407.293 | 31.7474 | Junction
Junction-99464 | 356814.6172 | 6668404.4883 | 31.8146 | Sink/User
Junction-99465 | 356836.9062 | 6668438.2148 | 31.2994 | Sink/User
Junction-99466 | 356809.5938 | 6668429.9648 | 31.1914 | Junction
Junction-99467 | 356802.0586 | 6668434.2227 | 30.9313 | Sink/User
Junction-99472 | 357595.3086 | 6668309.4883 | 16.2679 | Sink/User
Junction-99473 | 357576.0391 | 6668337.7734 | 17.0348 | Sink/User
Junction-99479 | 357456.0078 | 6668526.5586 | 20.2317 | Junction
Junction-99484 | 357427.2422 | 6668579.7617 | 22.4344 | Sink/User
Junction-99485 | 358084.6484 | 6668464.7305 | 13.7357 | Junction
Junction-99513 | 356885.8516 | 6668380.0195 | 30.4477 | Junction
Junction-99515 | 356884.0039 | 6668384.8477 | 30.6053 | Junction
Junction-99516 | 356876.7773 | 6668403.1992 | 31.6065 | Sink/User
Junction-99517 | 356881.8984 | 6668390.1992 | 30.8151 | Junction
Junction-99519 | 357131.125 | 6667873.5273 | 15.2583 | Sink/User
Junction-99525 | 357129.1172 | 6668432.0469 | 23.5154 | Junction
Junction-99526 | 357129.0859 | 6668433.6406 | 23.5779 | Junction
Junction-99528 | 357128.3242 | 6668001.5977 | 19.5084 | Sink/User
Junction-99534 | 356953.832 | 6667821.5586 | 11.2611 | Junction
Junction-99535 | 356959.2969 | 6667830.7031 | 11.6105 | Sink/User
Junction-99536 | 356935.0039 | 6667830.8125 | 11.7408 | Junction
Junction-99537 | 356933.7461 | 6667827.6484 | 11.6377 | Sink/User
Junction-99538 | 356939.3398 | 6667838.0938 | 12.0224 | Sink/User
Junction-99539 | 356919.0703 | 6667838.6719 | 12.2513 | Junction
Junction-99540 | 356872.8477 | 6667861.4297 | 13.7469 | Junction
Junction-99542 | 356867.8672 | 6667858.9141 | 13.7424 | Sink/User
Junction-99544 | 356888.6602 | 6667878.5195 | 14.8943 | Sink/User
Junction-99559 | 357419.1914 | 6667366.9258 | 6.0288 | Sink/User
Junction-99593 | 357040.4062 | 6667834.4609 | 12.0723 | Junction
Junction-99598 | 356636.6875 | 6667875.6875 | 21.1091 | Sink/User
Junction-99613 | 357324.9414 | 6668076.4961 | 27.9298 | Sink/User
Junction-99625 | 356894.3867 | 6668405.4805 | 31.3818 | Sink/User
Junction-99626 | 356929.2344 | 6668418.9023 | 30.5351 | Junction
Junction-99627 | 356925.4492 | 6668418.1367 | 30.7297 | Sink/User
Junction-99628 | 356937.0742 | 6668421.1289 | 30.5023 | Sink/User
Junction-99630 | 356935.2148 | 6668399.7148 | 29.6971 | Junction
Junction-99631 | 356935.0273 | 6668394.5508 | 30.1257 | Junction
Junction-99632 | 356937.1016 | 6668388.1797 | 30.7551 | Sink/User
Junction-99634 | 357434.3164 | 6667674.793 | 7.1877 | Junction
Junction-99635 | 357428.6328 | 6667671.5117 | 7.1407 | Sink/User
Junction-99645 | 357036.7852 | 6668234.2305 | 28.2103 | Sink/User
Junction-99647 | 359661.918 | 6667695.0703 | 17.677 | Sink/User
Junction-99651 | 359667.4609 | 6667723.8633 | 17.6868 | Junction
Junction-99653 | 359672.2031 | 6667725.8906 | 17.6549 | Sink/User
Junction-99655 | 358026.8086 | 6668557.3008 | 22.5436 | Sink/User
Junction-99668 | 357440.5352 | 6668360.2891 | 17.9526 | Sink/User
Junction-99671 | 357430.9688 | 6668363.6367 | 18.1689 | Junction
Junction-99690 | 357667.9141 | 6667918.3359 | 8.4574 | Junction
Junction-99693 | 357423.0703 | 6668356.0195 | 18.2658 | Junction
Junction-99701 | 357461.875 | 6668430.2969 | 19.8274 | Sink/User
Junction-99702 | 357179.6523 | 6667907.625 | 17.3743 | Junction
Junction-99703 | 357062.6523 | 6668424.3945 | 24.8793 | Junction
Junction-99723 | 359478.4844 | 6667644.6172 | 15.3271 | Junction
Junction-99727 | 359489.0195 | 6667661.2891 | 15.3394 | Sink/User
Junction-99755 | 356784.6211 | 6668003.8242 | 17.608 | Junction
Junction-99756 | 356796.5039 | 6668008.5391 | 17.8623 | Junction
Junction-99757 | 356792.6758 | 6668019.1445 | 18.0349 | Sink/User
Junction-99760 | 357053.0508 | 6668480.0586 | 26.6733 | Junction
Junction-99781 | 357721.668 | 6667697.4141 | 10.6177 | Junction
Junction-99783 | 357515.7422 | 6667433.125 | 6.8298 | Junction
Junction-99790 | 357533.5352 | 6668082.1562 | 17.581 | Sink/User
Junction-99794 | 357491.7891 | 6668449.6797 | 20.9165 | Sink/User
Junction-99803 | 357599.5859 | 6668448.3555 | 23.7851 | Sink/User
Junction-99816 | 358072.0078 | 6668998.1289 | 19.1902 | Junction
Junction-99818 | 358042.1914 | 6668992.125 | 18.285 | Sink/User
Junction-99819 | 359830.0273 | 6667805.0273 | 20.342 | Sink/User
Junction-99822 | 357618.6211 | 6667761.1133 | 8.1184 | Sink/User
Junction-99826 | 356859.9688 | 6668375.2227 | 31.1191 | Junction
Junction-99827 | 356850.8672 | 6668396.4805 | 31.6331 | Sink/User
Junction-99828 | 356816.0977 | 6668017.6172 | 18.0334 | Junction
Junction-99830 | 356758.3945 | 6667933.5312 | 16.7106 | Junction
Junction-99866 | 356976.1875 | 6668239.3242 | 23.7604 | Sink/User
Junction-99869 | 356766.0781 | 6668085.4336 | 21.9083 | Junction
Junction-99870 | 356747.0625 | 6668071.2695 | 21.2377 | Junction
Junction-99871 | 356745.6797 | 6668073.3164 | 21.3934 | Sink/User
Junction-99872 | 356736.1016 | 6668062.3008 | 20.8234 | Junction
Junction-99873 | 356733.4805 | 6668061.7656 | 20.8462 | Sink/User
Junction-99874 | 356741.8086 | 6668055.3242 | 20.2477 | Junction
Junction-99875 | 356740.2969 | 6668054.2344 | 20.2064 | Sink/User
Junction-99876 | 356749.0547 | 6668046.5156 | 19.5448 | Junction
Junction-99877 | 356754.5625 | 6668051.168 | 19.7552 | Sink/User
Junction-99878 | 356756.375 | 6668030.9883 | 18.5511 | Sink/User
Junction-99880 | 356755.1016 | 6667992.3086 | 17.1078 | Junction
Junction-99881 | 356756.1289 | 6667989.7422 | 17.0479 | Sink/User
Junction-99884 | 356981.375 | 6668414.0156 | 28.0053 | Junction
Junction-99889 | 357015.3984 | 6668413.6484 | 26.1211 | Junction
Junction-99890 | 357743.6602 | 6667639.6602 | 11.1474 | Junction
Junction-99902 | 357003.668 | 6668326.707 | 27.0489 | Sink/User
Junction-99936 | 356821.457 | 6668012.3281 | 17.9394 | Sink/User
Junction-99974 | 357331.0352 | 6668010.6992 | 27.7593 | Junction
Junction-100018 | 357119.4414 | 6668422.6602 | 23.2287 | Junction
Junction-100019 | 357118.3086 | 6668419.9609 | 23.1107 | Sink/User
Junction-100035 | 357122.1719 | 6667996.6289 | 19.1596 | Junction
Junction-100039 | 356790.5664 | 6668110.2539 | 22.4723 | Sink/User
Junction-100042 | 357675.8984 | 6667918.8203 | 8.355 | Sink/User
Junction-100043 | 357762.6016 | 6667876.0078 | 7.6811 | Sink/User
Junction-100050 | 357339.6172 | 6668010.8125 | 27.8556 | Junction
Junction-100052 | 357344.3984 | 6668002.582 | 28.0152 | Sink/User
Junction-100054 | 357388.9688 | 6668000.9531 | 28.2299 | Sink/User
Junction-100058 | 357453.1523 | 6668007.7148 | 25.4489 | Sink/User
Junction-100086 | 357576.2031 | 6667403.582 | 6.8963 | Junction
Junction-100094 | 357688.2109 | 6667396.8438 | 6.6567 | Junction
Junction-100096 | 357682.9375 | 6667369.2148 | 6.4761 | Sink/User
Junction-100097 | 357687.7461 | 6667373.875 | 6.5621 | Junction
Junction-100098 | 357691.707 | 6667372.5508 | 6.6357 | Sink/User
Junction-100100 | 357719.6914 | 6667387.2617 | 7.4115 | Sink/User
Junction-100102 | 357036.4766 | 6667819.4492 | 11.5478 | Sink/User
Junction-100103 | 357036.0547 | 6667834.0859 | 12.0044 | Sink/User
Junction-100104 | 357013.6641 | 6667796.9023 | 10.6749 | Sink/User
Junction-100105 | 356997.7969 | 6667811.8594 | 11.0559 | Sink/User
Junction-100107 | 357177.8594 | 6667665.1641 | 6.9481 | Sink/User
Junction-100110 | 357181.5938 | 6667706.0703 | 8.6997 | Junction
Junction-100111 | 357182.0195 | 6667709.7109 | 8.9643 | Sink/User
Junction-100121 | 358044.6016 | 6667395.4648 | 6.6288 | Junction
Junction-100124 | 357135.7109 | 6667187.8633 | 11.5469 | Sink/User
Junction-100156 | 357969.4805 | 6667286.582 | 6.2479 | Sink/User
Junction-100168 | 357338.0391 | 6668528.5273 | 21.2019 | Sink/User
Junction-100172 | 357738.6094 | 6668505.4336 | 36.3412 | Sink/User
Junction-100179 | 357150.9961 | 6668037.7578 | 26.5091 | Sink/User
Junction-100220 | 357324.957 | 6667955.4531 | 26.1886 | Sink/User
Junction-100224 | 357263.9766 | 6667945.6523 | 20.8209 | Junction
Junction-100225 | 357248.9883 | 6667949.2617 | 19.37 | Junction
Junction-100227 | 357263.3008 | 6667937.6133 | 20.2287 | Sink/User
Junction-100228 | 357257.6406 | 6667946.1562 | 20.1145 | Junction
Junction-100229 | 357257.8242 | 6667948.8945 | 20.2877 | Sink/User
Junction-100231 | 357204 | 6667925.1367 | 17.8259 | Sink/User
Junction-100239 | 357513.3281 | 6667411.6836 | 6.2882 | Junction
Junction-100240 | 357051.4219 | 6667738.6992 | 8.5765 | Sink/User
Junction-100241 | 357044.0625 | 6667743.3047 | 8.6819 | Sink/User
Junction-100245 | 356799.5586 | 6668098.9805 | 21.6723 | Junction
Junction-100246 | 356772.4805 | 6668090.7539 | 22.0728 | Junction
Junction-100247 | 356771.3203 | 6668092.5078 | 22.203 | Sink/User
Junction-100249 | 356772.1602 | 6668078.7109 | 21.3423 | Sink/User
Junction-100261 | 357124.9102 | 6667954.5312 | 17.9408 | Sink/User
Junction-100262 | 357124.9766 | 6668437.125 | 23.7957 | Sink/User
Junction-100264 | 357244.7031 | 6667637.9844 | 6.7564 | Sink/User
Junction-100266 | 357294.2812 | 6667637.0586 | 6.7328 | Junction
Junction-100267 | 357293.6016 | 6667631.6133 | 6.6947 | Sink/User
Junction-100269 | 357087.4531 | 6668411.9609 | 23.2821 | Sink/User
Junction-100271 | 356877.3008 | 6667880.8477 | 15.0585 | Sink/User
Junction-100272 | 356890.6406 | 6667852.2344 | 13.0717 | Junction
Junction-100273 | 356889.1914 | 6667851.2969 | 13.0525 | Sink/User
Junction-100274 | 356906.0781 | 6667844.7383 | 12.6475 | Junction
Junction-100275 | 356903.4648 | 6667839.6367 | 12.5086 | Sink/User
Junction-100277 | 356933.7188 | 6667865.2383 | 13.8176 | Junction
Junction-100278 | 356924.4844 | 6667868.6602 | 13.9899 | Sink/User
Junction-100287 | 357149.5547 | 6668438.9883 | 23.3965 | Junction
Junction-100288 | 356809.0938 | 6668085.5781 | 20.579 | Sink/User
Junction-100289 | 356808.2617 | 6668102.2617 | 22.2505 | Sink/User
Junction-100290 | 357048.5781 | 6668480.2266 | 26.6976 | Junction
Junction-100291 | 357053.6484 | 6668481.25 | 26.6884 | Sink/User
Junction-100292 | 357048.1797 | 6668482.5938 | 26.735 | Junction
Junction-100293 | 357031.6523 | 6668479.5508 | 26.6766 | Sink/User
Junction-100294 | 357043.1758 | 6668514.5195 | 26.0286 | Junction
Junction-100295 | 357069.0117 | 6668519.1758 | 25.0813 | Sink/User
Junction-100296 | 357026.4531 | 6668514.4609 | 26.5046 | Junction
Junction-100297 | 357026.9961 | 6668509.9727 | 26.7263 | Sink/User
Junction-100298 | 357006.3633 | 6668512.0781 | 27.2394 | Junction
Junction-100299 | 357005.9727 | 6668514.9219 | 27.1631 | Sink/User
Junction-100300 | 356995.3516 | 6668510.7148 | 27.6201 | Junction
Junction-100301 | 356995.5781 | 6668498.9375 | 27.7306 | Sink/User
Junction-100303 | 356993.1484 | 6668511.8594 | 27.665 | Sink/User
Junction-100305 | 357035.6133 | 6668515.8945 | 26.1322 | Junction
Junction-100318 | 359465.2656 | 6667550.4375 | 14.9707 | Junction
Junction-100332 | 357059.543 | 6668444.8281 | 25.4185 | Junction
Junction-100333 | 357053.6406 | 6668443.7969 | 25.5448 | Sink/User
Junction-100334 | 357059.6758 | 6668417.5703 | 24.837 | Sink/User
Junction-100335 | 357029.6523 | 6668430.1055 | 25.9687 | Sink/User
Junction-100336 | 357016.7812 | 6668403.918 | 25.8321 | Junction
Junction-100337 | 356911.5 | 6668387.8164 | 30.4068 | Junction
Junction-100338 | 356913.2656 | 6668378.9688 | 31.0419 | Sink/User
Junction-100339 | 356965.6562 | 6668453.5898 | 30.8522 | Sink/User
Junction-100340 | 356975.0859 | 6668453.6719 | 29.6274 | Sink/User
Junction-100357 | 357058.3711 | 6668453.4648 | 25.6982 | Junction
Junction-100359 | 357025.7969 | 6668788.1641 | 20.5357 | Junction
Junction-100368 | 358003.3828 | 6668715.6406 | 16.887 | Junction
Junction-100381 | 357276.4883 | 6668014.9375 | 23.9845 | Junction
Junction-100382 | 357276.3438 | 6668011.7578 | 24.1057 | Sink/User
Junction-100388 | 357391.5859 | 6667452.457 | 7.1689 | Junction
Junction-100402 | 357512.2617 | 6667337.6055 | 6.0012 | Sink/User
Junction-100403 | 357575.1719 | 6667357.5234 | 6.4801 | Sink/User
Junction-100420 | 359840.0898 | 6667898.6484 | 23.004 | Junction
Junction-100427 | 357003.6367 | 6667886.9492 | 15.4594 | Sink/User
Junction-100436 | 356963.5078 | 6668392.5469 | 29.5915 | Sink/User
Junction-100437 | 356978.957 | 6668396.9805 | 28.5369 | Sink/User
Junction-100438 | 357010.125 | 6668403.2695 | 26.1693 | Sink/User
Junction-100439 | 357026.4297 | 6668404.9219 | 25.479 | Sink/User
Junction-100440 | 357033.3398 | 6668533.4727 | 24.4376 | Junction
Junction-100441 | 357035.4648 | 6668533.8438 | 24.2665 | Sink/User
Junction-100442 | 357029.7969 | 6668532.9336 | 24.7117 | Sink/User
Junction-100443 | 357072.3281 | 6668481.9336 | 26.4064 | Sink/User
Junction-100444 | 357083.543 | 6668455.2773 | 25.2489 | Sink/User
Junction-101660 | 361883.8114 | 6668480.8958 | 13.5702 | Junction
Junction-101919 | 363261.5312 | 6671702.3086 | 12.9952 | Junction
Junction-102036 | 356961.082 | 6665831.418 | 27.4141 | Junction
Junction-102277 | 362191.125 | 6671762.8672 | 21.7511 | Junction
Junction-102637 | 356957.9648 | 6665836.2617 | 27.3495 | Sink/User
Junction-102990 | 363279.418 | 6671728.1016 | 13.5831 | Junction
Junction-103003 | 358286.8164 | 6668107.3945 | 10.4153 | Junction
Junction-103293 | 362067.8281 | 6671879.1953 | 25.8169 | Sink/User
Junction-103313 | 358360.293 | 6668281.3867 | 9.7817 | Junction
Junction-103322 | 362075.832 | 6671886.4062 | 27.0622 | Junction
Junction-103455 | 358404.3633 | 6668330.8633 | 10.168 | Junction
Junction-105118 | 365973.2773 | 6670138.0078 | 27.8814 | Sink/User
Junction-105140 | 365989.1797 | 6670189.5391 | 27.2794 | Junction
Junction-105274 | 357070.8633 | 6668289.9492 | 21.1166 | Junction
Junction-105276 | 357152.3047 | 6668294.2344 | 21.0874 | Junction
Junction-105282 | 357097.3438 | 6668289.4062 | 20.7739 | Junction
Junction-105411 | 362920.1445 | 6671149.3281 | 16.0356 | Sink/User
Junction-105540 | 363085.0742 | 6671470.8203 | 20.5954 | Junction
Junction-105543 | 363216.8125 | 6671740.2812 | 14.5917 | Sink/User
Junction-105560 | 363261.1367 | 6671701.6953 | 12.9893 | Junction
Junction-105562 | 357039.3945 | 6667784.4219 | 10.3388 | Sink/User
Junction-105810 | 363113.7109 | 6671495.7188 | 20.5241 | Sink/User
Junction-105811 | 363113.875 | 6671496.7031 | 20.5303 | Junction
Junction-105812 | 363114.0977 | 6671496.9258 | 20.5246 | Junction
Junction-105813 | 363114.5625 | 6671496.4805 | 20.5016 | Sink/User
Junction-105814 | 363114.7383 | 6671497.5664 | 20.5073 | Junction
Junction-106045 | 363037.6445 | 6671453.5391 | 19.7215 | Junction
Junction-106048 | 363043.125 | 6671450.6094 | 19.8361 | Junction
Junction-106055 | 363029.8086 | 6671428.0977 | 18.2855 | Junction
Junction-106057 | 362959.3945 | 6671330.8359 | 14.6369 | Junction
Junction-106088 | 363069.4336 | 6671484.9219 | 21.295 | Junction
Junction-106090 | 358066.2383 | 6667591.7031 | 5.802 | Sink/User
Junction-106092 | 358047.5508 | 6667587.5781 | 5.7464 | Junction
Junction-106326 | 357911.0039 | 6667643.0742 | 7.102 | Junction
Junction-106327 | 357911.2695 | 6667641.3984 | 7.0898 | Sink/User
Junction-106501 | 357909.3203 | 6667642.7891 | 7.1923 | Sink/User
Junction-106504 | 357948.6328 | 6667669.4297 | 7.3099 | Junction
Junction-106507 | 357904.6992 | 6667789.7461 | 7.4263 | Sink/User
Junction-107214 | 357957.4922 | 6667757.1602 | 6.5985 | Junction
Junction-111142 | 359709.7148 | 6667475.9727 | 5.8423 | Sink/User
Junction-111147 | 359712.5625 | 6667472.2109 | 5.7782 | Junction
Junction-111150 | 357024.7969 | 6665770.6641 | 30.7995 | Sink/User
Junction-111155 | 357023.2188 | 6665769.4336 | 30.6766 | Junction
Junction-111157 | 363373.7461 | 6671921.3867 | 14.7234 | Junction
Junction-111160 | 363377.4492 | 6671944.0742 | 15.3618 | Sink/User
Junction-111171 | 364443.4102 | 6671399.1719 | 10.1917 | Sink/User
Junction-111193 | 364464.5898 | 6671359.4492 | 8.1735 | Junction
Junction-111196 | 358238.5547 | 6668730.2617 | 11.9418 | Sink/User
Junction-111208 | 358216.4258 | 6668738.1016 | 12.5006 | Junction
Junction-111213 | 364329.6602 | 6671743.1641 | 8.0201 | Sink/User
Junction-111223 | 364337.6992 | 6671720.5469 | 7.3787 | Junction
Junction-111225 | 365598.2773 | 6670110.7344 | 26.8917 | Junction
Junction-111228 | 365593.8359 | 6670132.0234 | 27.4601 | Sink/User
Junction-114744 | 357252.1289 | 6666042.9297 | 35.2546 | Junction
Junction-114781 | 363136.4531 | 6672416.5469 | 21.9368 | Junction
Junction-115208 | 357489.8359 | 6666424.7695 | 36.0004 | Junction
Junction-115682 | 357023.3789 | 6669438.4453 | 54.1339 | Junction
Junction-116686 | 359647.2773 | 6667577.4648 | 12.3977 | Junction
Junction-116837 | 362670.8867 | 6671072.3359 | 16.7084 | Sink/User
Junction-116891 | 357139.3086 | 6667515.2227 | 6.3676 | Junction
Junction-116892 | 357073.75 | 6667520.4766 | 6.4858 | Sink/User
Junction-116901 | 357183.3047 | 6667509.5312 | 6.9523 | Junction
Junction-117566 | 357490.0078 | 6666465.8008 | 36.904 | Sink/User
Junction-117594 | 357234.6094 | 6666028.0039 | 36.057 | Sink/User
Junction-118151 | 357182.1641 | 6667500.0938 | 6.7958 | Sink/User
Junction-118160 | 359674.6953 | 6667556.8906 | 11.8834 | Sink/User
Junction-120721 | 362878.9258 | 6671451.9648 | 15.0422 | Junction
Junction-120722 | 362879.3438 | 6671452.457 | 15.0619 | Junction
Junction-120847 | 362880.375 | 6671448.6992 | 15.0326 | Junction
Junction-122930 | 357942.4095 | 6668102.5811 | 8.3201 | Sink/User
Junction-126962 | 366065.5508 | 6670399.4766 | 27.4452 | Junction
Junction-127158 | 366229.793 | 6670328.5039 | 23.4891 | Junction
Junction-127160 | 356954.5898 | 6668002.1289 | 18.8694 | Junction
Junction-127162 | 356952.8359 | 6668003.7969 | 18.7317 | Junction
Junction-127164 | 356950.8242 | 6668002.5273 | 18.7039 | Junction
Junction-127171 | 356954.6016 | 6668005.1523 | 18.752 | Junction
Junction-127174 | 362527.0352 | 6670868.3242 | 19.1994 | Junction
Junction-127181 | 362536.3711 | 6670878.9492 | 19.5033 | Junction
Junction-127182 | 362536.625 | 6670879.2656 | 19.5242 | Junction
Junction-127184 | 362542.6016 | 6670889.0898 | 19.9578 | Junction
Junction-127197 | 362536.4922 | 6670877.6953 | 19.4482 | Junction
Junction-127208 | 364416.7188 | 6671740.1523 | 8.2949 | Junction
Junction-127219 | 364407.8516 | 6671753.6641 | 8.3996 | Junction
Junction-127222 | 363241.3281 | 6672004.5898 | 15.3577 | Sink/User
Junction-127234 | 363237.1406 | 6671945.3477 | 14.163 | Junction
Junction-127246 | 356783.3047 | 6668003.1992 | 17.5532 | Junction
Junction-127265 | 362696.4531 | 6671044.2188 | 17.3919 | Junction
Junction-127268 | 362779.957 | 6670984.2734 | 15.9421 | Junction
Junction-127286 | 362774.3867 | 6670956.0977 | 15.6987 | Junction
Junction-127291 | 362612.4922 | 6670817.457 | 18.3932 | Junction
Junction-127293 | 366388.2383 | 6670420.6602 | 23.6391 | Sink/User
Junction-127300 | 366377.7891 | 6670449.8633 | 26.5585 | Junction
Junction-127302 | 365639.2969 | 6670175.3242 | 34.1852 | Sink/User
Junction-127314 | 362613.7656 | 6670826.9414 | 18.3875 | Junction
Junction-127332 | 365656.9492 | 6670150.1914 | 29.2413 | Junction
Junction-127340 | 365693.1367 | 6670223.4141 | 32.2756 | Sink/User
Junction-127376 | 365738.375 | 6670193.332 | 28.6184 | Junction
Junction-127378 | 356990.2773 | 6667865.6406 | 14.3766 | Junction
Junction-127380 | 356991.7539 | 6667864.9258 | 14.2621 | Junction
Junction-127382 | 357084.2383 | 6667865.8438 | 14.3904 | Junction
Junction-127383 | 357090.7266 | 6667868.5156 | 14.4521 | Junction
Junction-127385 | 357094.7617 | 6667870.2266 | 14.5461 | Junction
Junction-127386 | 357092.3711 | 6667869.1719 | 14.4876 | Junction
Junction-127387 | 357091.5625 | 6667868.8125 | 14.4686 | Junction
Junction-127406 | 357090.418 | 6667871.9336 | 14.654 | Junction
Junction-127409 | 357005.4961 | 6667859.7852 | 13.4746 | Junction
Junction-127410 | 357014.9727 | 6667868.0078 | 14.0568 | Sink/User
Junction-127411 | 356994.9688 | 6667871.2109 | 14.5551 | Junction
Junction-127412 | 356957.7773 | 6667880.9219 | 16.2399 | Junction
Junction-127413 | 356955.5312 | 6667876.4922 | 15.8001 | Sink/User
Junction-127414 | 356941.6953 | 6667883.0859 | 16.0168 | Junction
Junction-127417 | 356946.3633 | 6667887.3242 | 16.7302 | Junction
Junction-127438 | 356958.5547 | 6667881.7266 | 16.3661 | Junction
Junction-127442 | 356972.2695 | 6667874.6992 | 14.984 | Junction
Junction-127446 | 357003.0195 | 6667859.2383 | 13.4177 | Junction
Junction-127464 | 356987.7188 | 6667861.8555 | 14.2398 | Sink/User
Junction-127493 | 356978.8438 | 6667886.4883 | 16.2593 | Sink/User
Junction-127510 | 366376.8164 | 6670451.9453 | 26.6441 | Junction
Junction-127514 | 357324.0586 | 6667598.4648 | 6.7241 | Junction
Junction-127516 | 357327.6328 | 6667598.0508 | 6.7293 | Junction
Junction-127533 | 357323.1328 | 6667598.6172 | 6.7224 | Junction
Junction-127534 | 357328.3125 | 6667597.9922 | 6.7301 | Junction
Junction-127537 | 356878.75 | 6667873.2539 | 14.0771 | Junction
Junction-127538 | 356878.1953 | 6667873.4805 | 14.1136 | Junction
Junction-127596 | 356952.9219 | 6667899.6523 | 17.7113 | Sink/User
Junction-127650 | 363239.1289 | 6671913.6562 | 14.0149 | Sink/User
Junction-127924 | 357034.7227 | 6667843.2734 | 12.5928 | Junction
Junction-128160 | 357004.4766 | 6667858.5352 | 13.3834 | Junction
Junction-128162 | 357003.4141 | 6667855.4883 | 13.1789 | Sink/User
Junction-128164 | 357003.6758 | 6667858.9141 | 13.4021 | Junction
Junction-128230 | 362739.5352 | 6671054.8281 | 17.9016 | Junction
Junction-128231 | 362739.6094 | 6671054.5859 | 17.9058 | Sink/User
Junction-128233 | 362741.0586 | 6671054.9102 | 17.8162 | Sink/User
Junction-128234 | 362739.2891 | 6671055.6211 | 17.8886 | Junction
Junction-128246 | 356873.4648 | 6667861.1094 | 13.376 | Junction
Junction-128247 | 356877.9922 | 6667873.9883 | 14.1769 | Junction
Junction-128250 | 363239.3789 | 6671858.4336 | 14.9006 | Junction
Junction-128253 | 356782.0547 | 6667995.1562 | 17.4226 | Sink/User
Junction-128285 | 362779.7422 | 6670983.5938 | 15.9338 | Sink/User
Junction-128286 | 362780.1758 | 6670984.9766 | 15.9465 | Sink/User
Junction-128333 | 364418.6133 | 6671739.3633 | 8.3204 | Sink/User
Junction-128334 | 364417.3242 | 6671738.7617 | 8.3166 | Sink/User
Junction-128432 | 363153.6328 | 6672009.6016 | 17.7344 | Junction
Junction-128433 | 363145.9336 | 6672008.9297 | 18.2533 | Sink/User
Junction-128439 | 363655.0156 | 6671070.0352 | 10.4855 | Junction
Junction-128440 | 363662.3789 | 6671072.5938 | 10.0994 | Sink/User
Junction-128595 | 358357.375 | 6668173.5352 | 13.9997 | Sink/User
Junction-128600 | 358353.5859 | 6668128.2695 | 15.0213 | Sink/User
Junction-128637 | 358329.9062 | 6668145.375 | 12.0318 | Junction
Junction-128816 | 358332.1602 | 6668179.4141 | 11.1185 | Junction
Junction-128917 | 366336.3945 | 6670559.6992 | 23.8099 | Junction
Junction-129043 | 357859.957 | 6668931.1133 | 18.7325 | Junction
Junction-129097 | 362785.0859 | 6671078.4141 | 15.8532 | Junction
Junction-129103 | 357859.4727 | 6668915.7852 | 19.0691 | Junction
Junction-129106 | 364514.6953 | 6671666.4492 | 11.1914 | Junction
Junction-129107 | 364515.2734 | 6671666.7227 | 11.209 | Sink/User
Junction-129109 | 364517.9453 | 6671668.0352 | 11.279 | Sink/User
Junction-129111 | 364514.1797 | 6671666.5859 | 11.1941 | Junction
Junction-129113 | 364513.7891 | 6671667.4297 | 11.2346 | Junction
Junction-129143 | 364530.3516 | 6671669.5273 | 11.2464 | Junction
Junction-129145 | 362785.3867 | 6671079.1797 | 15.8395 | Junction
Junction-129148 | 362785.0938 | 6671079.4961 | 15.844 | Junction
Junction-129149 | 362785.1016 | 6671080.1367 | 15.8412 | Sink/User
Junction-129171 | 362786.2773 | 6671079.1953 | 15.8177 | Junction
Junction-129191 | 362838.6562 | 6671055.1016 | 15.8331 | Junction
Junction-129247 | 363497.75 | 6672325.957 | 14.1387 | Junction
Junction-129248 | 357860.3984 | 6668931.1094 | 18.7098 | Junction
Junction-129250 | 357866.0391 | 6668915.3555 | 18.03 | Junction
Junction-129256 | 362785.0898 | 6671077.9023 | 15.8573 | Junction
Junction-129272 | 363316.9258 | 6671833.1367 | 14.1935 | Sink/User
Junction-129282 | 363304.5156 | 6671821.3008 | 13.9941 | Junction
Junction-129285 | 363456.7812 | 6672186.5625 | 17.065 | Sink/User
Junction-129775 | 362627.7305 | 6671623.7969 | 18.2329 | Junction
Junction-130756 | 362786.8398 | 6670948.5977 | 15.5801 | Junction
Junction-131108 | 356871.1602 | 6667862.2539 | 13.4228 | Junction
Kantvik_EMP | 355459.8828 | 6664662.2539 | 10.2162 | Sink/User
Kummihovi_EMP | 355672.4883 | 6664548.4023 | 22.7685 | Sink/User
Neidonkallio_EMP_1 | 357047.3125 | 6669431.2383 | 52.7481 | Sink/User
Neidonkallio_EMP_2 | 357457.5742 | 6669242.1914 | 22.848 | Sink/User

## Output
Temperature (Celcius) | mdot_kg_per_s
130.5858 | 80.5268
130.2217 | 80.528
129.9496 | 80.5265
129.7695 | 80.5273
129.9496 | 80.5265
130.5436 | 80.5266
131.9078 | 80.5269
133.1341 | 80.5268
132.724 | 80.5261
131.7239 | 80.5266
131.5438 | 80.5271
129.5856 | 80.5277
128.9495 | 80.5274
128.3593 | 80.5276
128.2214 | 80.5278
128.3134 | 80.5271
128.7694 | 80.527
129.5856 | 80.5277
130.2217 | 80.528
131.0418 | 80.5272
131.8158 | 80.5267
132.1339 | 80.5303
131.7239 | 80.5266
131.0878 | 80.5265